## Cost Database
Account | Level | Account Name | Account Title | Standard Cost Equation? | Optional Variable | Optional Value | Sec Optional Variable | Sec Optional Value | Fixed Cost ($) | Unit Cost | Unit Cost (units) | Scaling Variable | Scaling Variable Ref Value | Units | Exponent | Dollar Year | Type | Source | Ref | Link | Notes | FOAK to NOAK Multiplier Type | Fixed Cost Low End | Fixed Cost High End | Fixed Cost Distribution | Unit Cost Low End | Unit Cost High End | Unit Cost Distribution | Exponent std | Exponent Max | Exponent Min | Exponent Distribution
10 | 0 | Capitalized Pre-Construction Costs | Capitalized Pre-Construction Costs
11 | 1 | Land Cost | Land Cost | standard | [5 empty] | 3800 | $/acres | Land Area |  | acres |  | 2022 | General | The average cost per acre for rural land in 2022 from the US Department of Agriculture | Abou-Jaoude, A., Lohse, C. S., Larsen, L. M., Guaita, N., Trivedi, I., Joseck, F. C., ... & Stein, A. (2024). Meta-analysis of advanced nuclear reactor cost estimations (No. INL/RPT-24-77048-Rev001). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_107010.pdf |  | No Learning | 0 | 0 | Lognormal | 3420 | 4940 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
12 | 1 | Site Permits | Site Permits | standard | [5 empty] | 10030 | $/MWe | Power MWe |  | MWe |  | 2022 | Labor | Data from SMR MHTGRs |  |  |  | No Learning | 0 | 0 | Lognormal | 9027 | 13039 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
13 | 1 | Plant Licensing | Plant Licensing | standard |  |  |  |  | 27025000 | [6 empty] | 2024 | Labor | NRC Website | Using data from the NRC website that the cost is between 45 and 70M https://www.nrc.gov/about-nrc/regulatory/licensing/general-fee-questions.pdf Also, using recent change to the NRC fees by a factor of 0.47 https://ignition-news.com/the-nrc-passes-new-rules-for-advanced-reactor-companies/#:~:text=Under%20a%20rule%20published%20in,2024%2C%20which%20takes%20effect%20Oct. | https://art.inl.gov/NGNP/INL%20Documents/Year%202012/Assessment%20of%20High%20Temperature%20Gas-Cooled%20Reactor%20-%20HTGR%20-%20Capital%20and%20Operating%20Costs.pdf |  | Licensing Learning | 21150000 | 32900000 | Uniform | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
14 | 1 | Plant Permits | Plant Permits | standard |  |  |  |  | 3000000 | [6 empty] | 2009 | Labor | NGNP project | Gandrik, A., B. Wallace, L. Demick, S. Melancon and M. Patterson (2011). "Assessment of high temperature gas-cooled reactor (HTGR) capital and operating costs." Idaho National Laboratory, TEV-1196, Idaho Falls, ID. |  |  | No Learning | 2700000 | 4500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
15 | 1 | Plant Studies | Plant Studies | standard |  |  |  |  | 5210451 | [6 empty] | 2024 | Labor | MARVEL Project (Labor-adjusted Cost) | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf | MARVEL's data were updated | No Learning | 4689405.9 | 7815676.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
20 | 0 | Capitalized Direct Costs | Capitalized Direct Costs
21 | 1 | Structures and Improvements | Structures and Improvements
211 | 2 | Site Preparation/ Yard Work | Site Preparation/ Yard Work
211.1 | 3 | Cleaning and Grubbing | Cleaning and Grubbing | standard | [5 empty] | 5862.8794 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 5276.5915 | 7621.7432 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.2 | 3 | Stripping Topsoil | Stripping Topsoil | standard | [5 empty] | 3411.716 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 3070.5444 | 4435.2308 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.3 | 3 | Excavation | Excavation | standard | [5 empty] | 32.004 | $/m^3 | Excavation Volume |  | m^3 |  | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 28.8036 | 41.6052 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212 | 2 | Reactor Island Civil Structures | Reactor Island Civil Structures
212.1 | 3 | Reactor Building Slab Roof | Reactor Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Reactor Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.2 | 3 | Reactor Building Basement | Reactor Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Reactor Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.3 | 3 | Reactor Building Walls | Reactor Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Reactor Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.4 | 3 | Reactor Building Liner | Reactor Building Liner | standard | [5 empty] | 6491.9267 | $/m^2 | Reactor Building Superstructure Area | 9373 | m^2 | 1 | 2018 | Lab and Mat and Equip | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | https://doi.org/10.1016/j.rser.2021.111880 |  | Onsite Learning | 0 | 0 | Lognormal | 5842.734 | 8439.5047 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.5 | 3 | Reactor Building HVAC | Reactor Building HVAC | standard | [5 empty] | 1731.9189 | $/MWt | Power MWt | 3417 | MWt | 0.8 | 2018 | Lab and Mat and Equip | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | https://doi.org/10.1016/j.rser.2021.111880 |  | Onsite Learning | 0 | 0 | Lognormal | 1558.727 | 2251.4946 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213 | 2 | Main Function Buildings | Main Function Buildings
213.1 | 3 | Energy conversion Building | Energy conversion Building
213.11 | 4 | Energy Conversion Building Slab Roof | Energy Conversion Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Turbine Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.12 | 4 | Energy Conversion Building Basement | Energy Conversion Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Turbine Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.13 | 4 | Energy Conversion Building Walls | Energy Conversion Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Turbine Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.2 | 3 | Control building | Control building
213.21 | 4 | Control Building Slab Roof | Control Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Control Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.22 | 4 | Control Building Basement | Control Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Control Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.23 | 4 | Control Building Walls | Control Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Control Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.3 | 3 | Integrated Heat Exchanger Building | Integrated Heat Exchanger Building |  | reactor type | GCMR
213.31 | 4 | Integrated Heat Exchanger Building Slab Roof | Integrated Heat Exchanger Building Slab Roof | standard | reactor type | GCMR |  |  |  | 1200 | $/m^3 | Integrated Heat Exchanger Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.32 | 4 | Integrated Heat Exchanger Building Basement | Integrated Heat Exchanger Building Basement | standard | reactor type | GCMR |  |  |  | 943.9 | $/m^3 | Integrated Heat Exchanger Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.33 | 4 | Integrated Heat Exchanger Building Walls | Integrated Heat Exchanger Building Walls | standard | reactor type | GCMR |  |  |  | 721.21 | $/m^3 | Integrated Heat Exchanger Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.34 | 4 | Integrated Heat Exchanger Building Liner | Integrated Heat Exchanger Building Liner | standard | reactor type | GCMR |  |  |  | 6491.9267 | $/m^2 | Integrated Heat Exchanger Building Superstructure Area | 9373 | m^2 | 1 | 2018 | Lab and Mat and Equip | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | https://doi.org/10.1016/j.rser.2021.111880 |  | Onsite Learning | 0 | 0 | Lognormal | 5842.734 | 8439.5047 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214 | 2 | Buildings to Support Main Function | Buildings to Support Main Function
214.1 | 3 | Fuel Management Buildings | Fuel Management Buildings
214.11 | 4 | Refueling Building | Refueling Building
214.111 | 5 | Refueling Building Slab Roof | Refueling Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Refueling Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 |  | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.112 | 5 | Refueling Building Basement | Refueling Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Refueling Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.113 | 5 | Refueling Building Walls | Refueling Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Refueling Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.12 | 4 | Spent Fuel Building | Spent Fuel Building
214.121 | 5 | Spent Fuel Building Slab Roof | Spent Fuel Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Spent Fuel Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.122 | 5 | Spent Fuel Building Basement | Spent Fuel Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Spent Fuel Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.123 | 5 | Spent Fuel Building Walls | Spent Fuel Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Spent Fuel Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.7 | 3 | Emergency and Start-up Power Systems Building | Emergency and Start-up Power Systems Building
214.71 | 4 | Emergency Building | Emergency Building
214.711 | 5 | Emergency Building Slab Roof | Emergency Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Emergency Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.712 | 5 | Emergency Building Basement | Emergency Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Emergency Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.713 | 5 | Emergency Building Walls | Emergency Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Emergency Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.72 | 4 | Diesel Generator | Diesel Generator | standard | [5 empty] | 2717311.5663 | $/MWt | Power MWt | 0.083 | MWt | 0.7 | 2024 | Equipment | MARVEL (for the cost of the diesel generator) The exponent is based on the work by Koruoush considering cost scaling from nuclear ad non nuclear power plants. When using the power as scaling variable, the exponent ranges between 0..6 and 0.8 so 0.7 is used here | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Stewart, W. R., & Shirvan, K. (2022). Capital cost estimation for advanced nuclear power plants. Renewable and Sustainable Energy Reviews, 155, 111880. | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf https://www.sciencedirect.com/science/article/pii/S1364032121011473 |  | Factory Other | 0 | 0 | Lognormal | 2445580.4096 | 3532505.0361 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.8 | 3 | Auxilliary Building | Auxilliary Building
214.81 | 4 | Maniplator Building | Maniplator Building
214.811 | 5 | Manipulator Building Slab Roof | Manipulator Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Manipulator Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 | Added a custom building for GCMR based on CAD drawing | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.812 | 5 | ManipulatorBuilding Basement | ManipulatorBuilding Basement | standard | [5 empty] | 943.9 | $/m^3 | Manipulator Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.813 | 5 | Manipulator Building Exterior Walls | Manipulator Building Exterior Walls | standard | [5 empty] | 721.21 | $/m^3 | Manipulator Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215 | 2 | Supply Chain Buildings | Supply Chain Buildings
215.1 | 3 | Storage Building | Storage Building
215.11 | 4 | Storage Building Slab Roof | Storage Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Storage Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.12 | 4 | Storage Building Basement | Storage Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Storage Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.13 | 4 | Storage Building Walls | Storage Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Storage Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.4 | 3 | Radwaste Building | Radwaste Building
215.41 | 4 | Radwaste Building Slab Roof | Radwaste Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Radwaste Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.42 | 4 | Radwaste Building Basement | Radwaste Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Radwaste Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.43 | 4 | Radwaste Building Walls | Radwaste Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Radwaste Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
22 | 1 | Reactor System | Reactor System
221 | 2 | Reactor Components | Reactor Components
221.1 | 3 | Reactor Vessel and Accessories | Reactor Vessel and Accessories
221.11 | 4 | Reactor Support | Reactor Support | standard | [5 empty] | 311.558 | $/Kg | Total Vessels Mass | 2447 | Kg | 0.85 | 2018 | Lab and Mat and Equip | PWR12-ME |  |  | Unit cost is the cost of support structure divided by the cost of guard vessel plus PCS | Factory Primary Structure | 0 | 0 | Lognormal | 280.4022 | 405.0254 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Guard Vessel Material | stainless_steel |  |  |  | 757.2077 | $/Kg | Guard Vessel Mass | 1587 | Kg |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 681.4869 | 984.37 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Guard Vessel Material | low_alloy_steel |  |  |  | 154.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 138.672 | 200.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Guard Vessel Material | incoloy |  |  |  | 444.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 399.672 | 577.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Vessel Material | stainless_steel |  |  | 3369444.6 | 1768.3558 | $/Kg | Vessel Mass | 860 |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  | Unit cost if the PCS cost (in MARVEL) divided by the PCS mass in MARVEL | Factory Primary Structure | 3032500.14 | 5054166.9 | Lognormal | 1591.5202 | 2298.8626 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Vessel Material | low_alloy_steel |  |  |  | 154.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 138.672 | 200.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Vessel Material | incoloy |  |  |  | 444.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 399.672 | 577.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.2 | 3 | Reactor Control Devices | Reactor Control Devices
221.21 | 4 | Reactivity Control System | Reactivity Control System
221.211 | 5 | Reactivity Control System Fabrication | Reactivity Control System Fabrication | standard | [5 empty] | 347890 | $/Drum | Drum Count |  |  |  | 2024 | Lab and Mat and Equip | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team | Gerstner, D., & Arafat, Y. (2023). MARVEL 90% Final Design Report (No. INL/RPT-23-74280-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | The scaling variable here is the total mass of all the control drums | Factory Drums | 0 | 0 | Lognormal | 313101 | 452257 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.212 | 5 | Installation | Installation | standard | [5 empty] | 80665.75 | $/Drum | Drum Count |  |  |  | 2024 | Lab and Equip | MARVEL Project |  |  |  | Factory Drums | 0 | 0 | Lognormal | 72599.175 | 104865.475 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.213 | 5 | Control Drums Materials (Absorber) | Control Drums Materials (Absorber) | standard | Control Drum Absorber | B4C_natural |  |  |  | 14285.7143 | $/Kg | Control Drum Absorber Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Other | 0 | 0 | Lognormal | 12857.1429 | 18571.4286 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.213 | 5 | Control Drums Materials (Absorber) | Control Drums Materials (Absorber) | standard | Control Drum Absorber | B4C_enriched |  |  |  | 10064 | $/Kg | Control Drum Absorber Mass |  |  |  | 2023 | Material | Prosser et al., 2023 |  |  |  | Factory Other | 0 | 0 | Lognormal | 9057.6 | 13083.2 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | BeO |  |  |  | 10062.8931 | $/Kg | Control Drum Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory BeO | 0 | 0 | Lognormal | 9056.6038 | 13081.761 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | Be |  |  |  | 44736.8421 | $/Kg | Control Drum Reflector Mass | 19 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Be | 0 | 0 | Lognormal | 40263.1579 | 58157.8947 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | Graphite |  |  |  | 80 | $/Kg | Control Drum Reflector Mass |  |  |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other | 0 | 0 | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.215 | 5 | Control System Drive Mechanism | Control System Drive Mechanism | standard | [5 empty] | 74759 | $/Drum | Drum Count |  |  |  | 2023 | Lab and Mat and Equip | Prosser et al., 2023 | First-Principles Cost Estimation of a Sodium Fast Reactor Nuclear Plant. INL/RPT-23-74316 Table 38, 39 |  | Bottom-up Estimation of components with nuclear escalation + contingency | Factory Drums | 0 | 0 | Lognormal | 67283.1 | 97186.7 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.3 | 3 | Non-Fuel Core Internals | Non-Fuel Core Internals | standard
221.31 | 4 | Reflector | Reflector | standard | Reflector | BeO |  |  | 120231 | 10062.8931 | $/Kg | Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team | Gerstner, D., & Arafat, Y. (2023). MARVEL 90% Final Design Report (No. INL/RPT-23-74280-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). |  | Factory BeO | 108207.9 | 180346.5 | Lognormal | 9056.6038 | 13081.761 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.31 | 4 | Reflector | Reflector | standard | Reflector | Be |  |  |  | 44736.8421 | $/Kg | Reflector Mass | 19 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team |  |  | Factory Be | 0 | 0 | Lognormal | 40263.1579 | 58157.8947 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.31 | 4 | Reflector | Reflector | standard | Reflector | Graphite |  |  |  | 80 | $/Kg | Reflector Mass |  |  |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other | 0 | 0 | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.31 | 4 | Reflector | Reflector | standard | Reflector | Al2O3 |  |  |  | 134.1 | $/Kg | Reflector Mass |  |  |  | 2017 | Material | NTRD-FCO-2018-000439 |  |  |  | Factory Other | 0 | 0 | Lognormal | 120.69 | 174.33 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.32 | 4 | Shield | Shield
221.321 | 5 | In Vessel Shield Materials | In Vessel Shield Materials | standard | In Vessel Shield Material | B4C_natural |  |  | 647990.6 | 14285.7143 | $/Kg | In Vessel Shield Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Other | 583191.54 | 971985.9 | Lognormal | 12857.1429 | 18571.4286 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.322 | 5 | Out The Vessel Shield Materials | Out The Vessel Shield Materials | standard | Out Of Vessel Shield Material | WEP |  |  |  | 20 | $/Kg | Out Of Vessel Shield Mass | 925.3 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Other | 0 | 0 | Lognormal | 18 | 26 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | Graphite |  |  |  | 80 | $/Kg | Moderator Mass |  | Kg |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other |  |  | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | YHx |  |  |  | 15200 | $/Kg | Moderator Mass |  | Kg |  | 2017 | Material |  |  |  |  | Factory Other |  |  | Lognormal | 13680 | 19760 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | ZrH |  |  |  | 1520 | $/Kg | Moderator Mass |  | Kg |  | 2017 | Material | the Fuel SA&I Cost Basis Report | Abou-Jaoude, A., C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman, N. Stauff, K. Shirvan and A. Stein (2024). Meta-Analysis of Advanced Nuclear Reactor Cost Estimations, Idaho National Laboratory (INL), Idaho Falls, ID (United States). |  |  | Factory Other |  |  | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.34 | 4 | Moderator (Booster) | Moderator (Booster) | standard | Moderator Booster | YHx |  |  |  | 15200 | $/Kg | Moderator Booster Mass |  | Kg |  | 2017 | Material |  |  |  |  | Factory Other |  |  | Lognormal | 13680 | 19760 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.34 | 4 | Moderator (Booster) | Moderator (Booster) | standard | Moderator Booster | Graphite |  |  |  | 80 | $/Kg | Moderator Booster Mass |  | Kg |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other |  |  | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.34 | 4 | Moderator (Booster) | Moderator (Booster) | standard | Moderator Booster | ZrH |  |  |  | 1520 | $/Kg | Moderator Booster Mass |  | Kg |  | 2017 | Material | the Fuel SA&I Cost Basis Report | Abou-Jaoude, A., C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman, N. Stauff, K. Shirvan and A. Stein (2024). Meta-Analysis of Advanced Nuclear Reactor Cost Estimations, Idaho National Laboratory (INL), Idaho Falls, ID (United States). |  |  | Factory Other |  |  | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222 | 2 | Main Heat Transport System | Main Heat Transport System
222.1 | 3 | Fluid Circulation Drive System | Fluid Circulation Drive System
222.11 | 4 | Primary Pump | Primary Pump | nonstandard | Primary Pump | Yes |  |  |  | 8818.5 | $/(kg.sec) | Primary Pump Mechanical Power |  |  | 0.71 | 2003 | Lab and Mat and Equip | Data from non-nuclear power plant + Ratio of safety grade pump nomalized cost compared to non-safety grade pump is btween 10 and 15 (12.5 ratio was used, from the EEDB (Ganda 2019, Figure 23) | Roosen, P., Uhlenbruck, S., & Lucas, K. (2003). Pareto optimization of a combined cycle power system as a decision support tool for trading off investment vs. operating costs. International Journal of Thermal Sciences, 42(6), 553-560. Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). | https://www.sciencedirect.com/science/article/pii/S1290072903000218 https://publications.anl.gov/anlpubs/2019/06/152862.pdf |  | Factory Other | 0 | 0 | Lognormal | 7936.65 | 11464.05 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.12 | 4 | Secondary Pump | Secondary Pump | nonstandard | Secondary Pump | Yes |  |  |  | 705.48 | $/(kg.sec) | Secondary Pump Mechanical Power |  |  | 0.71 | 2003 | Lab and Mat and Equip | Data from non-nuclear power plant |  |  |  | Factory Other | 0 | 0 | Lognormal | 634.932 | 917.124 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.13 | 4 | Compressor | Compressor | nonstandard | reactor type | GCMR |  |  |  | 7100000 | unitless |  |  |  |  | 2020 | Lab and Mat and Equip | ANL/NSE-20/28 | Hoffman et al. (2020). Improvement of ACCERT Algorithm - FY20 (No. ANL/NSE-20/28). Argonne National Laboratory.(ANL), Argonne, IL (United States). |  | Implemented on the python side. Chosen over default due to uncertainty in compressor Pressure Ratio changes based on reactor TH | Factory Other | 0 | 0 | Lognormal | 6390000 | 9230000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.2 | 3 | Reactor Heat Transfer Piping System | Reactor Heat Transfer Piping System | standard | [5 empty] | 20000 | $/MWe | Power MWe |  |  |  | 2017 | Equipment | From EEBD | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 18000 | 26000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.3 | 3 | Heat Exchangers | Heat Exchangers
222.31 | 4 | Primary Heat Exchanger | Primary Heat Exchanger | standard | HX Material | SS316 |  |  |  | 50 | $/Kg | Primary HX Mass |  | Kg |  | 2004 | Equipment | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology. |  |  | Factory Other | 0 | 0 | Lognormal | 45 | 65 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.31 | 4 | Primary Heat Exchanger | Primary Heat Exchanger | standard | HX Material | 800H |  |  |  | 120 | $/Kg | Primary HX Mass |  | Kg |  | 2013 | Equipment | Non Nuclear Plants | Yoon, S.-J., P. Sabharwall and E.-S. Kim (2013). Analytical study on thermal and mechanical design of printed circuit heat exchanger, Idaho National Lab.(INL), Idaho Falls, ID (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 108 | 156 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger | standard | HX Material | SS316 |  |  |  | 50 | $/Kg | Secondary HX Mass |  | Kg |  | 2004 | Equipment | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology. |  |  | Factory Other | 0 | 0 | Lognormal | 45 | 65 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger | standard | HX Material | 800H |  |  |  | 120 | $/Kg | Secondary HX Mass |  | Kg |  | 2013 | Equipment | Non Nuclear Plants | Yoon, S.-J., P. Sabharwall and E.-S. Kim (2013). Analytical study on thermal and mechanical design of printed circuit heat exchanger, Idaho National Lab.(INL), Idaho Falls, ID (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 108 | 156 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.5 | 3 | Initial Coolant Inventory | Initial Coolant Inventory | standard | Coolant | Helium |  |  |  | 170 | $/Kg | Onsite Coolant Inventory |  | Kg |  | 2024 | Material | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | https://doi.org/10.3929/ethz-b-000709311 | Vendor Quoate (Linde) for 3000 cylinders of 99.999% purity Helium. 3000 cylinders correspond to ~4 MT of He. | No Learning | 0 | 0 | Lognormal | 153 | 221 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.5 | 3 | Initial Coolant Inventory | Initial Coolant Inventory | standard | Coolant | NaK |  |  |  | 118 | $/Kg | Onsite Coolant Inventory |  | Kg |  | 2023 | Material |  |  |  |  | No Learning |  |  |  | 106.2 | 153.4 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.6 | 3 | Integrated Heat Transfer Vessel | Integrated Heat Transfer Vessel |  | reactor type | GCMR
222.61 | 4 | Integrated Heat Transfer Vessel | Integrated Heat Transfer Vessel | standard | reactor type | GCMR |  |  |  | 50 | $/Kg | Integrated Heat Transfer Vessel Mass |  | Kg |  | 2004 | Lab and Mat and Equip | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology. |  | Custom Accounts to model the vessel that houses the PCHE, Circulator, and Pipe Connections. These are assumed to be SA508 for now but use the same unit-cost as SS PCHE | Factory Other | 0 | 0 | Lognormal | 45 | 65 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.62 | 4 | Integrated Heat Transfer System Support | Integrated Heat Transfer System Support | standard | reactor type | GCMR |  |  |  | 8.1938 | $/Kg | Integrated Heat Transfer Vessel Mass | 387000 | Kg | 0.85 | 2018 | Lab and Mat and Equip | PWR12-ME | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology. |  |  | Factory Other | 0 | 0 | Lognormal | 7.3744 | 10.652 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
223 | 2 | Safety Systems | Safety Systems
223.2 | 3 | Reactor Cavity Cooling System (Rvacs) | Reactor Cavity Cooling System (Rvacs)
223.21 | 4 | Rvacs (Cooling Vessel) | Rvacs (Cooling Vessel) | standard | [5 empty] | 757.2077 | $/Kg | Cooling Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 681.4869 | 984.37 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
223.22 | 4 | Rvacs (Intake Vessel) | Rvacs (Intake Vessel) | standard | [5 empty] | 757.2077 | $/Kg | Intake Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 681.4869 | 984.37 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
226 | 2 | Other Reactor Plant Equipment | Other Reactor Plant Equipment | standard | reactor type | LTMR |  |  | 456297 | [6 empty] | 2024 | Equipment | MARVEL |  |  |  | Factory Other | 410667.3 | 684445.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
226 | 2 | Other Reactor Plant Equipment | Other Reactor Plant Equipment | standard | reactor type | GCMR |  |  |  | 118207.7741 | unitless | Primary Loop Mass Flow Rate | 610.21 | kg/s | 0.6 | 2023 | Lab and Mat and Equip | DOE-ET-34222-T1 | 1170 MWt HTGR Steamer Cogeneration Plant Design and Cost Study, United Engineers & Constructors Inc. Philadelphia, Pennsylvania. 1980] | https://www.osti.gov/servlets/purl/5084245 | Cost scalated based on Park et al., 2024 - Bottom-up …. | Factory Other | 0 | 0 | Lognormal | 106386.9966 | 153670.1063 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
227 | 2 | Reactor Instrumentation and Control (I&C) | Reactor Instrumentation and Control (I&C) | standard |  |  |  |  | 8500000 | [6 empty] | 2023 | Lab and Equip | Shirvan et al., 2023 | Shirvan et al,. (2023). UO2-fueled microreactors: Near-term solutions to emerging marktets. Nuclear Engineering and Design. | https://doi.org/10.1016/j.nucengdes.2023.112470 | Cost based on FOAK Digital I&C with 2-out-of-4 voting logic | Factory Other | 7650000 | 12750000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
228 | 2 | Reactor Plant Miscellaneous Items | Reactor Plant Miscellaneous Items | standard |  |  |  |  | 30960 | [6 empty] | 2024 | Lab and Mat and Equip | MARVEL |  |  |  | Factory Other | 27864 | 46440 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23 | 1 | Energy Conversion System | Energy Conversion System
232 | 2 | Energy Applications | Energy Applications
232.1 | 3 | Electricity Generation Systems | Electricity Generation Systems | standard | [5 empty] | 12504 | $/kWe | BoP Power kWe | 1 |  | 0.777 | 2023 | Lab and Mat and Equip | INL/RPT-24-80433 Rev.1 | INL/RPT-24-80433 Rev.1 | https://www.osti.gov/biblio/2447366 |  | Non-nuclear off-the-shelf | 0 | 0 | Lognormal | 11253.6 | 16255.2 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
236 | 2 | Common Instrumentation & Controls | Common Instrumentation & Controls | standard |  |  |  |  | 1000000 | [6 empty] | 2023 | Lab and Mat and Equip | Shirvan et al., 2023 | Shirvan et al,. (2023). UO2-fueled microreactors: Near-term solutions to emerging marktets. Nuclear Engineering and Design. | https://doi.org/10.1016/j.nucengdes.2023.112470 |  | Factory Other | 900000 | 1500000 | Lognormal
24 | 1 | Electrical Equipment | Electrical Equipment
241 | 2 | Switchgear | Switchgear | standard | [5 empty] | 12609.0098 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip | EEDB PWR12-ME + Stewart and Shirvan (2022) Scales PWR12-ME costs with simplifications based on Stewart and Srhivan (2022) | Stewart, W. R., & Shirvan, K. (2022). Capital cost estimation for advanced nuclear power plants. Renewable and Sustainable Energy Reviews, 155, 111880. |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 11348.1088 | 16391.7127 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
242 | 2 | Station Service Equipment | Station Service Equipment | standard | [5 empty] | 10483.0781 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 9434.7703 | 13628.0016 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
243 | 2 | Switchboards | Switchboards | standard | [5 empty] | 3404.0615 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 3063.6554 | 4425.28 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
244 | 2 | Protective Equipment | Protective Equipment | standard | [5 empty] | 9776.1468 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 8798.5321 | 12708.9908 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
245 | 2 | Electrical Structure & Wiring Container | Electrical Structure & Wiring Container | standard | [5 empty] | 52720.7025 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 47448.6323 | 68536.9133 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
246 | 2 | Power & Control Wiring | Power & Control Wiring | standard | [5 empty] | 39871.5712 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 35884.4141 | 51833.0426 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
25 | 1 | Initial Fuel Inventory | Initial Fuel Inventory
251 | 2 | First Core Mining | First Core Mining | standard | [5 empty] | 184 | $/Kg | Natural Uranium Mass |  |  |  | 2022 | Material | INL Cost Basis Report & Meta analysis for the nuclear reactor costs UO2-fueled microreactors: Near-term solutions to emerging markets | Abou-Jaoude, Abdalla, et al. Meta-Analysis of Advanced Nuclear Reactor Cost Estimations. No. INL/RPT-24-77048-Rev001. Idaho National Laboratory (INL), Idaho Falls, ID (United States), 2024. Abou-Jaoude, A., Y. Arafat, A. Foss, and B. Dixon. 2021. “An Economics-by-Design Approach Applied to a Heat Pipe Microreactor Concept.” INL/EXT-21-63067, Rev. 000, Idaho National Laboratory, Idaho Falls, Idaho. https://doi.org/10.2172/1811894. Kororush Shirvan, Jacopo Buongiorno, Ruaridh MacDonald, Bradley Dunkin, Sacit Cetiner, Earl Saito, Thomas Conboy, Charles Forsberg, UO2-fueled microreactors: Near-term solutions to emerging markets, Nuclear Engineering and Design |  |  | No Learning | 0 | 0 | Lognormal | 165.6 | 239.2 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
252 | 2 | First Core Conversion | First Core Conversion | standard | [5 empty] | 15.1 | $/Kg | Natural Uranium Mass |  |  |  | 2022 | Material |  |  |  |  | No Learning | 0 | 0 | Lognormal | 13.59 | 19.63 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
253 | 2 | First Core Enrichment | First Core Enrichment | nonstandard | [5 empty] | 184.2 | $/SWU | SWU |  |  | 1 | 2022 | Material |  |  |  |  | No Learning | 0 | 0 | Lognormal | 165.78 | 239.46 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | No | Fuel | TRIGA_fuel |  | 1520 | $/Kg | Uranium Mass |  |  |  | 2023 | Material |  |  |  |  | Factory Other | 0 | 0 | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | No | Fuel | UO2 |  | 250 | $/Kg | Uranium Mass |  |  |  | 2023 | Material |  |  |  |  | Factory Other | 0 | 0 | Lognormal | 225 | 325 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | Yes |  |  |  | 10000 | $/Kg | Uranium Mass |  |  |  | 2009 | Material |  |  |  |  | Factory Other | 0 | 0 | Lognormal | 9000 | 13000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
26 | 1 | Miscellaneous Equipment (Cranes) | Miscellaneous Equipment (Cranes) | standard |  |  |  |  | 1000000 | [6 empty] | 2021 | Equipment | A study for the mass manufacruing and factory fabrication of microreactors | Abou-Jaoude, A., Arafat, Yasir, Foss, Andrew Wilkin, and Dixon, Brent W (2021). An Economics-by-Design Approach Applied to a Heat Pipe Microreactor Concept. 2021. Idaho National Laboratory: Idaho Falls, ID, Idaho National Laboratory. |  |  | Factory Other | 900000 | 1500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
30 | 0 | Capitalized Indirect Services Cost | Capitalized Indirect Services Cost
31 | 1 | Factory & field indirect costs | Factory & field indirect costs
32 | 1 | Factory and construction supervision | Factory and construction supervision
33 | 1 | Startup Costs | Startup Costs | standard |  |  |  |  | 2407166.4 | [6 empty] | 2024 | Lab and Equip | MARVEL |  |  |  | Onsite Learning | 2166449.76 | 3610749.6 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
34 | 1 | Shipping and Transportation Costs | Shipping and Transportation Costs | standard |  |  |  |  | 832641.4 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 749377.26 | 1248962.1 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
35 | 1 | Engineering Services | Engineering Services | standard |  |  |  |  | 620313.5877 | [6 empty] | 2024 | Labor |  |  |  |  | Onsite Learning | 558282.229 | 930470.3816 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
36 | 1 | PM/CM Services | PM/CM Services | standard |  |  |  |  | 416958.936 | [6 empty] | 2024 | Labor |  |  |  |  | Onsite Learning | 375263.0424 | 625438.404 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
40 | 0 | Capitalized training costs | Capitalized training costs
41 | 1 | staff recruitment and training | staff recruitment and training | standard |  |  |  |  | 300000 | [6 empty] | 2024 | Labor |  | Al-Dawood, Khaldoon and Hanna, Botros and Balla, Sai and de Oliveira, Rodrigo and Garcia, Samuel and McCarthy, Dan and Bolisetti, Chandrakanth and Lindley, Ben and Abou-Jaoude, Abdalla, Open-Source Microreactor Design Models for Technoeconomic Assessment. | https://papers.ssrn.com/sol3/papers.cfm?abstract_id=5163464 |  | No Learning | 270000 | 450000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
60 | 0 | Capitalized Financial Costs | Capitalized Financial Costs
62 | 1 | Interest | Interest
70 | 0 | Annualized O&M Cost | Annualized O&M Cost
71 | 1 | O&M Staff | O&M Staff
711 | 2 | Operators | Operators | nonstandard | [5 empty] | 178500 | $/FTE | Number of Operators |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
712 | 2 | Remote Monitoring Technicians | Remote Monitoring Technicians | nonstandard | Operation Mode | Autonomous |  |  |  | 178500 | $/FTE | Reactors Monitored Per Operator |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
713 | 2 | Security Staff | Security Staff | nonstandard | [5 empty] | 178500 | $/FTE | Security Staff Per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
72 | 1 | Variable Non-Fuel Costs | Variable Non-Fuel Costs
721 | 2 | Coolant | Coolant | nonstandard | Coolant | Helium |  |  |  | 170 | $/Kg | Replacement Coolant Inventory |  | Kg |  | 2024 | Material | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | https://doi.org/10.3929/ethz-b-000709311 | Vendor Quoate (Linde) for 3000 cylinders of 99.999% purity Helium. 3000 cylinders correspond to ~4 MT of He. | No Learning | 0 | 0 | Lognormal | 153 | 221 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
721 | 2 | Coolant | Coolant | nonstandard | Coolant | NaK |  |  |  | 118 | $/Kg | Replacement Coolant Inventory |  | Kg |  | 2023 | Material | MARVEL Project (communication with MARVEL Team) |  |  | Vendor Quotes | No Learning | 0 | 0 | Lognormal | 106.2 | 153.4 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
73 | 1 | Regulatory Costs | Regulatory Costs | standard |  |  |  |  | 107180 | [6 empty] | 2024 | Labor | NRC annual fees for operating reactors in FY25 is $5,359,000 One assumption could be to consider a single fee for the fleet of microreactors. Proposed cost = $5,359,000 per year / (100 reactors per fleet) Another assumption (anecdotal evidence) is that licensing fee cost is 1-to-1 with the utility cost to support. | https://www.federalregister.gov/documents/2025/02/19/2025-02779/fee-schedules-fee-recovery-for-fiscal-year-2025 | https://www.federalregister.gov/documents/2025/02/19/2025-02779/fee-schedules-fee-recovery-for-fiscal-year-2025 |  | Licensing Learning | 96462 | 160770 | Lognormal
75 | 1 | Capital Plant Expenditures | Capital Plant Expenditures | [14 empty] | Venneri, (2023) and INL/EXT-21-63067 | Venneri, (2023) and INL/EXT-21-63067 |  | Implemented on non_direct_cost.py Cost is scaled as a fraction of CAPEX unless specific parameters are added to indicate more/less frequent replacements (e.g. GCMR)
751 | 2 | Annualized RPV Replacements | Annualized RPV Replacements | [14 empty] | Venneri, (2023) and INL/EXT-21-63067 | Venneri, (2023) and INL/EXT-21-63067 |  | Implemented on non_direct_cost.py Cost is scaled as a fraction of CAPEX unless specific parameters are added to indicate more/less frequent replacements (e.g. GCMR)
752 | 2 | Annualized Core Barrel Replacements | Annualized Core Barrel Replacements
753 | 2 | Annualized Moderator Replacements | Annualized Moderator Replacements
754 | 2 | Annualized Reflector Replacements | Annualized Reflector Replacements
755 | 2 | Annualized Reactivity Control Replacements | Annualized Reactivity Control Replacements
756 | 2 | Annualized Integrated Heat Transfer System Replacements | Annualized Integrated Heat Transfer System Replacements
759 | 2 | Annualized Misc. Replacements | Annualized Misc. Replacements
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost | [17 empty] | Implemented on non_direct_cost.py The cost is scaled as a fraction of CAPEX (15%)
80 | 0 | Annualized Fuel Cost | Annualized Fuel Cost
81 | 1 | Refueling Operations | Refueling Operations | nonstandard | [5 empty] | 178500 | $/FTE | Number of Operators |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
82 | 1 | Additional Nuclear Fuel | Additional Nuclear Fuel
83 | 1 | Spent Fuel Management | Spent Fuel Management | standard | [5 empty] | 1 | $/MWeHour | Annual Electricity Production |  |  | 1 | 2024 | Lab and Mat and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 0.9 | 1.3 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
Note on J5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the average of two values in the NRC website
Note on N80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since the cost of the BeO of the drums was not available, the cost of the BeO reflector is divided by its mass to get a unit cost for the BeO
Note on N81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since the cost of the BeO of the drums was not available, the cost of the BeO reflector is divided by its mass to get a unit cost for the BeO
Note on A83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added control rod/drum drive mechanism. Assuming: 1drum:1drive n_rod:1drive (Reactor design dependent) Reply: Ganda 2018: reports a cost of 610,000 $/drive (based on CE 1978 LMFBR cost), which is also quoted by Sai
Note on A85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todo: Update when we get feedback on BeO/Be costs
Note on A86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todo: Update when we get feedback on BeO/Be costs
Note on N90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cost data about B4C are based on the B4C of the control drums
Note on L100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The primary pump needs to be expensive!!
Note on K119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline Cost: 8844770 1978USD Escalation (to 2023): 8.155
Note on J145: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The cost is multiplied by 0.5 since the shipping included international shipping
Note on C157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Variable costs that are not fuel-based, such as borated water, control rods, burnable poisons, and other consumable Reply: For the GCMR, likley includes replacement coolant, CO2 refill, etc.
Note on C161: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Upgrades to maintain or improve plant capacity, meet future regulatory requirements, or plant life extensions. These costs are considered "sustaining capital" for continued plant operation and performance. Reply: Will allocate vessel, internals, IHX replacement, etc.

## MARVEL_Cost
Account ID | Account Title | TOTAL COST (2024 USD)
10 | Capitalized Pre-Construction Costs | 5210451
15 | Plant Studies | 5210451
20 | Capitalized Direct Costs | 30295715.422
21 | Structures and Improvements | 2799006.732
211 | Site Preparation/Yard Work
212 | Reactor Island Civil Structures | 2573469.872
213 | Main Function Buildings
214 | Buildings to Support Main Function | 225536.86
214.7 | Emergency and Start-up Power Systems | 225536.86
217 | Miscellaneous Other Structures
22 | Reactor System | 17586712.57
221 | Reactor Components | 8937296.6
221.1 | Reactor vessel and accessories | 2004852
221.11 | Reactor support | 762382.4
221.12 | Outer vessel structure | 1201688.6
221.13 | Inner vessel structure | 40781
221.2 | Reactor control devices | 2114223
221.21 | Reactivity control system | 2114223
221.211 | Reactivity Control System Fabrication | 1391560
221.212 | Installation | 322663
221.213 | Control Drums Materials (Absorber) | 400000
221.214 | Control Drums Materials (Reflector)
221.3 | Non-fuel core internals | 4818221.6
221.31 | Reflector | 4170231
221.311 | Reflector (Materials: BeO) | 3200000
221.312 | Reflector (Materials: Be Metal) | 850000
221.313 | Reflector (installation | 120231
221.32 | Shield | 647990.6
221.33 | Moderator | 0
222 | Main Heat Transport System | 5908950.6
222.1 | Fluid circulation drive system | 0
222.2 | Reactor Heat Hransfer Piping System | 4890230.6
222.21 | Reactor Heat Hransfer Piping System (Mat) | 1520786
222.22 | Reactor Heat Hransfer Piping System (Fabrication) | 3341486
222.23 | Reactor Heat Hransfer Piping System (Installation) | 27958.6
222.3 | Heat Exchangers | 0
222.4 | Pressurizer System | 0
222.5 | Initial Heat Transfer Fluid Inventory | 1018720
224 | Radioactive Byproduct Processing Systems
226 | Other Reactor Plant Equipment | 456297
227 | Reactor Instrumentation and Control (I&C) | 2253208.37
228 | Reactor Plant Miscellaneous Items | 30960
23 | Energy Conversion System | 0
232 | Energy Applications | 0
232.1 | Electricity Generation Systems | 0
24 | Electrical Equipment | 73415.62
244 | Protective Systems Equipment | 1627.02
245 | Electrical Raceway Systems | 0
246 | Power and Control Cables and Wiring | 71788.6
25 | Initial Fuel Inventory | 9836580.5
254 | First Core Fuel Assembly Fabrication | 9836580.5
26 | Miscellaneous Equipment
30 | Capitalized Indirect Services Cost | 6442742.5237
31 | Factory & Field Indirect Costs | 1333020.8
317 | Field Shops | 1333020.8
33 | Startup Costs | 2407166.4
331 | Commissioning and Trial Test Runs | 2407166.4
331.3 | Initial Fuel Loading Operations | 215000
331.5 | Test Runs | 2192166.4
34 | Shipping and Transportation Costs | 1665282.8
341 | Fuel Shipping and Transportation | 1635355.8
345 | Other Shipping and Transportation Costs | 29927
35 | Engineering Services | 620313.5877
351 | Off-Site | 257261.4
352 | On-Site | 363052.1877
36 | PM/CM Services | 416958.936
361 | Off-Site
362 | On-Site | 416958.936
40 | Capitalized Training Costs | 4169765
41 | Staff Recruitment and Training | 4169765
50 | Capitalized Supplementary Costs | 16408781.6
54 | Decommissioning | 16408781.6
60 | Capitalized Financial Costs | 6160606
61 | Escalation | 6160606
70 | Annualized O&M Cost | 2456659.2
71 | O&M Staff | 2456659.2
Non-Recurrung Costs | Non-Recurrung Costs | 33779050.1383

## Design Variables
Variable | Value | Units | Description
Overall System
Thermal power | 83 | kWth | —
Electric Power | 20 | kWe
Core outer radius | 5.5 | inches | —
Reflector outer radius | 16.5 | inches | —
Fuel
Fuel mass | 145.3 | kg | UZrH
U Weight fraction | 30 | wt% | U/UZrH
U enrichment | 19.75 | wt% | High-assay low-enriched uranium (HALEU)
Pins | 36 | # | —
Reflector
Outer reflector material | BeO | — | 99% theoretical density
Elements | 124 | # | Quarter plates
Reflector plate thickness | 1 | inches | —
Reflector plate volume | 818.4 | cm3/plate | —
Mass of BeO reflector | 318 | Kg
Insert volume | 570 | cm3/plate | —
Mass of Be-metal reflector | 0.019 | MT | —
Control Elements
Control drums | 4 | # | —
Shutdown rods | 1 | # | —
Control drum elements | 124 | # | Discs
Drum disc thickness | 1 | inches | —
Drum reflector volume | 880.8 | cm3/plate | BeO 99%
Mass of drum reflector | 309 | Kg | —
Drum poison volume | 49.2 | cm3/plate | B4C
Mass of drum poison | 14 | Kg | —
Mass of rod poison | 14 | Kg | B4C
Instruments and Controls
Control cabinet | 5 |  | —
Instrument cabinet | 2 |  | —
Nuclear input/output (IO) | 9 |  | —
Non-nuclear IO | 213 |  | —
Stirling engine IO | 48 | — | These should be excluded if there no stirling engine?
TOTAL | 277
Shielding in Vessel
Stainless Steel cans | 54.2 | Kg | Stainless Steel cans of the boron carbide shielding material (SS316H)
Gamma shield material | 56.3 | Kg | Gamma shield material inside the guard vessel (of Tungsten)
Neutron shield material in the guard vessel | 39.7 | Kg | made of natural B4C powder and is located above the core (a donut around the core barrel)—
Boron Carbine shielding | 95.3 | Kg | made of natural B4C (called base shield) below the core
Radial (lead) | 2571.9 | Kg | lead
Radial (WEP) | 925.3 | Kg | made of Water Extended Polyster (WEP)
Shielding in Pit
Mass of the pit neutron shielding | 8.3 | MT | Approximated 6-in.-thick covering whole pit and made of Water-extruded poly (WEP)
Heat Transfer
Mass of coolant | 156 | Kg | —
Number of loops | 4 | # | —
Mass of PCSs | 0.86 | MT | SS316H
Subassembly Structure Masses
Reactor support frame | 1.11 | MT | —
Guard vessel | 1.587 | MT | —

## Inflation Adjustment
Year | General | Labor | Material | Equipment | Lab and Mat and Equip | Lab and Equip
1985 | 2.4641 | 3.1849 | 3.0545 | 3.8306 | 3.3566 | 3.5077
1986 | 2.4153 | 3.0852 | 3.0607 | 3.7331 | 3.293 | 3.4092
1987 | 2.3571 | 2.9916 | 2.9992 | 3.6991 | 3.23 | 3.3453
1988 | 2.2768 | 2.8748 | 2.8406 | 3.5246 | 3.08 | 3.1997
1989 | 2.1908 | 2.7813 | 2.7498 | 3.3127 | 2.9479 | 3.047
1990 | 2.1116 | 2.6589 | 2.7466 | 3.2241 | 2.8765 | 2.9415
1991 | 2.0426 | 2.554 | 2.7291 | 3.1182 | 2.8004 | 2.8361
1992 | 1.9972 | 2.4751 | 2.6817 | 2.99 | 2.7156 | 2.7325
1993 | 1.9509 | 2.3964 | 2.5547 | 2.8241 | 2.5917 | 2.6102
1994 | 1.9101 | 2.3109 | 2.4545 | 2.7417 | 2.5024 | 2.5263
1995 | 1.8708 | 2.2707 | 2.3663 | 2.6949 | 2.4439 | 2.4828
1996 | 1.8373 | 2.215 | 2.3528 | 2.6375 | 2.4018 | 2.4263
1997 | 1.8061 | 2.1583 | 2.3124 | 2.576 | 2.3489 | 2.3671
1998 | 1.786 | 2.0934 | 2.3237 | 2.5207 | 2.3126 | 2.3071
1999 | 1.7611 | 2.024 | 2.3013 | 2.5047 | 2.2767 | 2.2644
2000 | 1.7221 | 1.9301 | 2.2793 | 2.4782 | 2.2292 | 2.2042
2001 | 1.6841 | 1.8435 | 2.3007 | 2.3994 | 2.1812 | 2.1214
2002 | 1.6583 | 1.783 | 2.2814 | 2.3771 | 2.1472 | 2.08
2003 | 1.6263 | 1.7217 | 2.2333 | 2.3372 | 2.0974 | 2.0294
2004 | 1.5838 | 1.6722 | 2.0346 | 2.2508 | 1.9859 | 1.9615
2005 | 1.5356 | 1.6186 | 1.9376 | 2.163 | 1.9064 | 1.8908
2006 | 1.4896 | 1.566 | 1.8228 | 1.9965 | 1.7951 | 1.7813
2007 | 1.4503 | 1.5071 | 1.7936 | 1.8327 | 1.7111 | 1.6699
2008 | 1.4228 | 1.455 | 1.6724 | 1.7874 | 1.6383 | 1.6212
2009 | 1.4141 | 1.4394 | 1.7367 | 1.7643 | 1.6468 | 1.6018
2010 | 1.3972 | 1.424 | 1.6891 | 1.7753 | 1.6295 | 1.5996
2011 | 1.3689 | 1.409 | 1.6335 | 1.7021 | 1.5815 | 1.5555
2012 | 1.3439 | 1.387 | 1.5962 | 1.5912 | 1.5248 | 1.4891
2013 | 1.3214 | 1.3588 | 1.5699 | 1.5349 | 1.4879 | 1.4469
2014 | 1.2988 | 1.3395 | 1.532 | 1.4777 | 1.4497 | 1.4086
2015 | 1.2868 | 1.312 | 1.5385 | 1.4366 | 1.4291 | 1.3743
2016 | 1.2747 | 1.2847 | 1.536 | 1.4153 | 1.412 | 1.35
2017 | 1.2523 | 1.2535 | 1.4823 | 1.3824 | 1.3727 | 1.318
2018 | 1.2243 | 1.2201 | 1.3936 | 1.3336 | 1.3157 | 1.2768
2019 | 1.2041 | 1.1832 | 1.3937 | 1.3 | 1.2923 | 1.2416
2020 | 1.1885 | 1.1509 | 1.3736 | 1.2822 | 1.2689 | 1.2165
2021 | 1.1365 | 1.1172 | 1.0828 | 1.2259 | 1.142 | 1.1715
2022 | 1.0616 | 1.0737 | 0.96194 | 1.0847 | 1.0401 | 1.0792
2023 | 1.0242 | 1.0296 | 0.99021 | 1.0049 | 1.0082 | 1.0172
2024 | 1 | 1 | 1 | 1 | 1 | 1

## Economics Parameters
Parameter | Value | Note | Reference | Notes
indirect to direct field-related cost | 0.06539
FTEs Per Onsite Operator (24/7) | 5
FTEs Per Offsite Operator (24/7) | 5
FTEs Per Security Staff (24/7) | 5
Hours Per FTE | 1800
Work Hours Per Shift | 10
Maintenance to Direct Cost Ratio | 0.01
Onsite Learning | 0.08 | FOAK to NOAK Learning Rates | Assessment of Factory Fabrication Considerations for Nuclear Microreactors 10.1080/00295450.2023.2206779 | Calculated based on Refernce Paper + Gyutae's work. Refer to TEM Slides for rationale and methodology
No Learning | 0
Licensing Learning | 0
Factory Primary Structure | 0.18443
Factory Drums | 0.24138
Factory Other | 0.22963
Factory Be | 0.41505
Factory BeO | 0.39915
Non-nuclear off-the-shelf | 0.05 |  | Park, et al., Bottom-up levelized cost estimation of low-enriched and low-pressure nuclear batteries. Nuclear Engineering and Design. 2025. | For off-the-shelf commercial components that are not produced in the FB Factory