## cost estimate
Account | Account Title | FOAK Estimated Cost ($2024) | NOAK Estimated Cost ($2024) | FOAK Estimated Cost std ($2024) | NOAK Estimated Cost std ($2024)
10 | Capitalized Pre-Construction Costs | 38100246 | 38100246 | 4110007 | 4110007
11 | Land Cost | 77459 | 77459 | 12413 | 12413
12 | Site Permits | 68566 | 68566 | 10795 | 10795
13 | Plant Licensing | 26835517 | 26835517 | 3398672 | 3398672
14 | Plant Permits | 4994824 | 4994824 | 1102191 | 1102191
15 | Plant Studies | 6123878 | 6123878 | 1336113 | 1336113
20 | Capitalized Direct Costs | 110710113 | 40486719 | 13789259 | 8054369
21 | Structures and Improvements | 12629265 | 3022676 | 6329242 | 1132977
211 | Site Preparation/ Yard Work | 192516 | 110631 | 21035 | 12088
211.1 | Cleaning and Grubbing | 111789 | 64240 | 16428 | 9440
211.2 | Stripping Topsoil | 66760 | 38364 | 11108 | 6383
211.3 | Excavation | 13967 | 8026 | 2003 | 1151
212 | Reactor Island Civil Structures | 1645102 | 945375 | 391770 | 225135
212.1 | Reactor Building Slab Roof | 184508 | 106029 | 27650 | 15889
212.2 | Reactor Building Basement | 143192 | 82287 | 22991 | 13212
212.3 | Reactor Building Walls | 154093 | 88551 | 23257 | 13365
212.4 | Reactor Building Liner | 1043306 | 599547 | 391010 | 224698
212.5 | Reactor Building HVAC | 120002 | 68960 | 58306 | 33506
213 | Main Function Buildings | 74135 | 42602 | 5116 | 2940
213.1 | Energy conversion Building | 49291 | 28325 | 4736 | 2721
213.11 | Energy Conversion Building Slab Roof | 15627 | 8980 | 2222 | 1277
213.12 | Energy Conversion Building Basement | 11787 | 6773 | 1943 | 1116
213.13 | Energy Conversion Building Walls | 21876 | 12571 | 3391 | 1949
213.2 | Control building | 24843 | 14276 | 1938 | 1114
213.21 | Control Building Slab Roof | 7767 | 4463 | 1127 | 647
213.22 | Control Building Basement | 6128 | 3521 | 867 | 498
213.23 | Control Building Walls | 10948 | 6291 | 1541 | 885
214 | Buildings to Support Main Function | 10678198 | 1901473 | 6331999 | 1118894
214.7 | Emergency and Start-up Power Systems Building | 10641593 | 1880438 | 6332029 | 1118910
214.72 | Diesel Generator | 10641593 | 1880438 | 6332029 | 1118910
214.8 | Auxilliary Building | 36604 | 21035 | 3161 | 1816
214.81 | Maniplator Building | 36604 | 21035 | 3161 | 1816
214.811 | Manipulator Building Slab Roof | 6301 | 3621 | 1024 | 588
214.812 | ManipulatorBuilding Basement | 17972 | 10327 | 2512 | 1443
214.813 | Manipulator Building Exterior Walls | 12330 | 7085 | 1850 | 1063
215 | Supply Chain Buildings | 39313 | 22591 | 3669 | 2108
215.1 | Storage Building | 39313 | 22591 | 3669 | 2108
215.11 | Storage Building Slab Roof | 15089 | 8671 | 2616 | 1503
215.12 | Storage Building Basement | 11852 | 6811 | 1972 | 1133
215.13 | Storage Building Walls | 12371 | 7109 | 2022 | 1162
22 | Reactor System | 56214050 | 11461156 | 4136441 | 800635
221 | Reactor Components | 35653798 | 7216244 | 2700287 | 583235
221.1 | Reactor Vessel and Accessories | 13977333 | 3607277 | 1877588 | 484568
221.11 | Reactor Support | 2291056 | 591276 | 392220 | 101224
221.13 | Inner Vessel Structure | 11686277 | 3016000 | 1773175 | 457622
221.2 | Reactor Control Devices | 16669290 | 2724166 | 1733756 | 279743
221.21 | Reactivity Control System | 16669290 | 2724166 | 1733756 | 279743
221.211 | Reactivity Control System Fabrication | 8888857 | 1418223 | 1543088 | 246200
221.212 | Installation | 2065075 | 329484 | 284317 | 45362
221.213 | Control Drums Materials (Absorber) | 3519669 | 621948 | 495497 | 87557
221.214 | Control Drums Materials (Reflector) | 244075 | 43129 | 41579 | 7347
221.215 | Control System Drive Mechanism | 1951612 | 311381 | 299389 | 47767
221.3 | Non-Fuel Core Internals | 5007173 | 884800 | 532905 | 94167
221.31 | Reflector | 1162483 | 205418 | 137697 | 24332
221.311 | Radial Reflector | 783566 | 138461 | 129388 | 22863
221.312 | Axial Reflector | 378917 | 66957 | 63154 | 11159
221.32 | Shield | 349337 | 61730 | 90333 | 15962
221.322 | Out The Vessel Shield Materials | 349337 | 61730 | 90333 | 15962
221.33 | Moderator | 515770 | 91139 | 81501 | 14401
221.34 | Moderator (Booster) | 2979581 | 526511 | 457207 | 80791
222 | Main Heat Transport System | 2950056 | 1133075 | 298838 | 127205
222.1 | Fluid Circulation Drive System | 1465889 | 259032 | 238258 | 42101
222.13 | Compressor | 1465889 | 259032 | 238258 | 42101
222.2 | Reactor Heat Transfer Piping System | 358697 | 63384 | 59557 | 10524
222.3 | Heat Exchangers | 382379 | 67568 | 60264 | 10649
222.31 | Primary Heat Exchanger | 382379 | 67568 | 60264 | 10649
222.5 | Initial Coolant Inventory | 743090 | 743090 | 108605 | 108605
223 | Safety Systems | 3166507 | 559542 | 311162 | 54984
223.2 | Reactor Cavity Cooling System (Rvacs) | 3166507 | 559542 | 311162 | 54984
223.21 | Rvacs (Cooling Vessel) | 1526138 | 269678 | 219554 | 38796
223.22 | Rvacs (Intake Vessel) | 1640368 | 289863 | 232558 | 41094
226 | Other Reactor Plant Equipment | 4630922 | 818314 | 2216095 | 391598
227 | Reactor Instrumentation and Control (I&C) | 9778148 | 1727862 | 2376854 | 420005
228 | Reactor Plant Miscellaneous Items | 34616 | 6116 | 7540 | 1332
23 | Energy Conversion System | 17278628 | 11690715 | 10570114 | 7512970
232 | Energy Applications | 16159751 | 11493002 | 10562252 | 7511996
232.1 | Electricity Generation Systems | 16159751 | 11493002 | 10562252 | 7511996
236 | Common Instrumentation & Controls | 1118877 | 197712 | 256976 | 45409
24 | Electrical Equipment | 10235641 | 7279707 | 3326001 | 2365490
241 | Switchgear | 817377 | 581328 | 433678 | 308437
242 | Station Service Equipment | 733001 | 521319 | 388739 | 276476
243 | Switchboards | 293690 | 208875 | 155541 | 110623
244 | Protective Equipment | 774349 | 550726 | 393030 | 279528
245 | Electrical Structure & Wiring Container | 4100089 | 2916031 | 2531818 | 1800658
246 | Power & Control Wiring | 3517134 | 2501427 | 2241814 | 1594404
25 | Initial Fuel Inventory | 13000697 | 6793586 | 1729651 | 1152808
251 | First Core Mining | 3306400 | 3306400 | 497564 | 497564
252 | First Core Conversion | 269051 | 269051 | 35254 | 35254
253 | First Core Enrichment | 1885879 | 1885879 | 918371 | 918371
254 | First Core Fuel Assembly Fabrication | 7539365 | 1332254 | 1269805 | 224382
26 | Miscellaneous Equipment (Cranes) | 1351828 | 238876 | 293209 | 51811
30 | Capitalized Indirect Services Cost | 11779599 | 4950298 | 1679804 | 775248
31 | Factory & field indirect costs | 5631508 | 1711551 | 881806 | 504910
32 | Factory and construction supervision | 1312325 | 459821 | 840312 | 241935
33 | Startup Costs | 2751226 | 1581021 | 642239 | 369069
34 | Shipping and Transportation Costs | 899749 | 517050 | 179542 | 103176
35 | Engineering Services | 706158 | 405801 | 154984 | 89063
36 | PM/CM Services | 478631 | 275050 | 107179 | 61592
40 | Capitalized training costs | 345086 | 345086 | 72757 | 72757
41 | staff recruitment and training | 345086 | 345086 | 72757 | 72757
60 | Capitalized Financial Costs | 2777713 | 1447796 | 272387 | 164439
62 | Interest | 2777713 | 1447796 | 272387 | 164439
70 | Annualized O&M Cost | 7532079 | 2735850 | 520002 | 193800
71 | O&M Staff | 1060009 | 1060009 | 134499 | 134499
711 | Operators | 6108 | 6108 | 1009 | 1009
712 | Remote Monitoring Technicians | 115969 | 115969 | 29869 | 29869
713 | Security Staff | 937931 | 937931 | 131907 | 131907
72 | Variable Non-Fuel Costs | 91562 | 91562 | 15585 | 15585
721 | Coolant | 91562 | 91562 | 15585 | 15585
73 | Regulatory Costs | 120276 | 120276 | 25183 | 25183
75 | Capital Plant Expenditures | 6190429 | 1427140 | 492841 | 130424
752 | Annualized Core Barrel Replacements | 2103393 | 542844 | 319150 | 82366
753 | Annualized Moderator Replacements | 92832 | 16404 | 14669 | 2592
754 | Annualized Reflector Replacements | 209233 | 36972 | 24783 | 4379
755 | Annualized Reactivity Control Replacements | 3000277 | 490318 | 312055 | 50350
759 | Annualized Misc. Replacements | 784693 | 340600 | 132389 | 80101
78 | Annualized Decommissioning Cost | 69801 | 36862 | 6801 | 4209
80 | Annualized Fuel Cost | 2396185 | 1278978 | 312878 | 208380
81 | Refueling Operations | 1833 | 1833 | 302 | 302
82 | Additional Nuclear Fuel | 2339973 | 1222766 | 311317 | 207492
83 | Spent Fuel Management | 54378 | 54378 | 8478 | 8478
OCC | Overnight Capital Cost | 160935045 | 83882350 | 15781554 | 9527307
OCC per kW | Overnight Capital Cost per kW | 26822 | 13980 | 2630 | 1587
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 147934347 | 77088763 | 15774220 | 9553002
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 24655 | 12848 | 2629 | 1592
TCI | Total Capital Investment | 163712758 | 85330146 | 16053941 | 9691747
TCI per kW | Total Capital Investment per kW | 27285 | 14221 | 2675 | 1615
AC | Annualized Cost | 9928265 | 4014828 | 591347 | 281127
AC per MWh | Annualized Cost per MWh | 190 | 77 | 11 | 5
LCOE | Levelized Cost Of Energy ($/MWh) | 415 | 194 | 29 | 16

## Parameters
Parameter | Value
plotting | N
cross_sections_xml_location | /projects/MRP_MOUSE/openmc_data/endfb-viii.0-hdf5/cross_sections.xml
simplified_chain_thermal_xml | /projects/MRP_MOUSE/openmc_data/simplified_thermal_chain11.xml
reactor type | GCMR
TRISO Fueled | Yes
Fuel | UN
Enrichment | 0.1975
UO2 atom fraction | 0.7
Reflector | Graphite
Matrix Material | Graphite
Moderator | Graphite
Moderator Booster | ZrH
Coolant | Helium
Common Temperature | 850
Control Drum Absorber | B4C_enriched
Control Drum Reflector | Graphite
HX Material | SS316
Fuel Pin Materials | ['UN', 'buffer_graphite', 'PyC', 'SiC', 'PyC']
Fuel Pin Radii | [0.025, 0.035, 0.039, 0.0425, 0.047]
Compact Fuel Radius | 0.6225
Packing Fraction | 0.3
Coolant Channel Radius | 0.35
Moderator Booster Radius | 0.55
Lattice Pitch | 2.25
Assembly Rings | 6
Core Rings | 5
Assembly FTF | 19.4856
Reflector Thickness | 27.393
Axial Reflector Thickness | 27.393
Core Radius | 124.8209
Active Height | 250
Drum Radius | 9
Drum Absorber Thickness | 1
Drum Height | 304.786
Drum Count | 24
All Drums Volume | 1860462.5098
Control Drum Absorber Mass | 327.9926
Control Drum Reflector Mass | 2941.5214
Control Drums Mass | 3269.514
All Drums Area | 6104.16
Reflector Mass | 9683.4839
Axial Reflector Mass | 4558.7179
Moderator Mass | 6360.3037
Moderator Booster Mass | 1217.375
Power MWt | 15
Thermal Efficiency | 0.4
Heat Flux Criteria | 0.9
Burnup Steps | [0.1, 0.2, 0.5, 1.0, 2.0, 5.0, 10.0, 15.0, 20.0, 30.0, 40.0, 50.0, 60.0, 80.0, 100.0, 120.0]
Power MWe | 6
Number Of TRISO Particles Per Compact Fuel | 209946
Total Number of TRISO Particles | 1165410246
Heat Flux | 0.016388
Fuel Lifetime | 2648
Mass U235 | 80971.7344
Mass U238 | 327918.6126
Uranium Mass | 408.8903
Natural Uranium Mass | 17333.3951
Fuel Tail Waste Mass | 16924.5048
SWU | 16803.2375
Primary Loop Purification | TRUE
Secondary HX Mass | 0
Compressor Pressure Ratio | 4
Compressor Isentropic Efficiency | 0.8
Primary Loop Count | 2
Primary Loop per loop load fraction | 0.5
Primary Loop Inlet Temperature | 573.15
Primary Loop Outlet Temperature | 823.15
Secondary Loop Inlet Temperature | 563.15
Secondary Loop Outlet Temperature | 773.15
Primary Loop Pressure Drop | 50000
Primary HX Mass | 1567.2086
Coolant Mass Flow Rate | 11.554
Primary Loop Mass Flow Rate | 5.777
Primary Loop Compressor Power | 108437.0872
BoP Count | 2
BoP per loop load fraction | 0.5
BoP Power kWe | 3000
Integrated Heat Transfer Vessel Thickness | 0
Integrated Heat Transfer Vessel Material | SA508
Integrated Heat Transfer Vessel Outer Volume | 0
Integrated Heat Transfer Vessel Mass | 0
In Vessel Shield Thickness | 0
In Vessel Shield Inner Radius | 124.8209
In Vessel Shield Material | B4C_natural
Out Of Vessel Shield Thickness | 39.37
Out Of Vessel Shield Material | WEP
Out Of Vessel Shield Effective Density Factor | 0.5
In Vessel Shield Outer Radius | 124.8209
Vessel Radius | 124.8209
Vessel Thickness | 1
Vessel Lower Plenum Height | 2.848
Vessel Upper Plenum Height | 47.152
Vessel Upper Gas Gap | 0
Vessel Bottom Depth | 32.129
Vessel Material | stainless_steel
Gap Between Vessel And Guard Vessel | 0
Guard Vessel Thickness | 0
Guard Vessel Material | low_alloy_steel
Gap Between Guard Vessel And Cooling Vessel | 5
Cooling Vessel Thickness | 0.5
Cooling Vessel Material | stainless_steel
Gap Between Cooling Vessel And Intake Vessel | 4
Intake Vessel Thickness | 0.5
Intake Vessel Material | stainless_steel
Vessels Total Radius | 135.3209
Vessel Height | 354.786
Vessels Total Height | 397.415
Guard Vessel Radius | 125.8209
Cooling Vessel Radius | 130.8209
Intake Vessel Radius | 134.8209
Vessel Mass | 3131.1612
Guard Vessel Mass | 0
Cooling Vessel Mass | 1421.0834
Intake Vessel Mass | 1477.4645
Total Vessels Mass | 6029.7092
RPV Outer Radius | 125.8209
RPV Outer Height | 421.044
In Vessel Shield Mass | 0
Outer Shield Outer Radius | 174.6909
Out Of Vessel Shield Mass | 19881.017
Operation Mode | Autonomous
Number of Operators | 2
Levelization Period | 60
Refueling Period | 7
Emergency Shutdowns Per Year | 0.2
Startup Duration after Refueling | 2
Startup Duration after Emergency Shutdown | 14
Reactors Monitored Per Operator | 10
Security Staff Per Shift | 1
Onsite Coolant Inventory | 2012.0096
Replacement Coolant Inventory | 503.0024
Annual Coolant Supply Frequency | 1
A75: Vessel Replacement Period (cycles) | 1
A75: Core Barrel Replacement Period (cycles) | 1
A75: Reflector Replacement Period (cycles) | 1
A75: Drum Replacement Period (cycles) | 1
Mainenance to Direct Cost Ratio | 0.015
A78: CAPEX to Decommissioning Cost Ratio | 0.15
Land Area | 18
Escalation Year | 2024
Excavation Volume | 412.605
Reactor Building Slab Roof Volume | 95.0976
Reactor Building Basement Volume | 95.0976
Reactor Building Exterior Walls Volume | 129.9564
Reactor Building Superstructure Area | 77
Integrated Heat Exchanger Building Slab Roof Volume | 0
Integrated Heat Exchanger Building Basement Volume | 0
Integrated Heat Exchanger Building Exterior Walls Volume | 0
Integrated Heat Exchanger Building Superstructure Area | 0
Turbine Building Slab Roof Volume | 5.9448
Turbine Building Basement Volume | 5.9448
Turbine Building Exterior Walls Volume | 14.2072
Control Building Slab Roof Volume | 5.9448
Control Building Basement Volume | 5.9448
Control Building Exterior Walls Volume | 14.2072
Manipulator Building Slab Roof Volume | 4.7566
Manipulator Building Basement Volume | 17.8374
Manipulator Building Exterior Walls Volume | 15.9195
Refueling Building Slab Roof Volume | 0
Refueling Building Basement Volume | 0
Refueling Building Exterior Walls Volume | 0
Spent Fuel Building Slab Roof Volume | 0
Spent Fuel Building Basement Volume | 0
Spent Fuel Building Exterior Walls Volume | 0
Emergency Building Slab Roof Volume | 0
Emergency Building Basement Volume | 0
Emergency Building Exterior Walls Volume | 0
Storage Building Slab Roof Volume | 11.76
Storage Building Basement Volume | 11.76
Storage Building Exterior Walls Volume | 15.768
Radwaste Building Slab Roof Volume | 0
Radwaste Building Basement Volume | 0
Radwaste Building Exterior Walls Volume | 0
Interest Rate | 0.07
Construction Duration | 12
Debt To Equity Ratio | 0.5
Annual Return | 0.0475
NOAK Unit Number | 100
Number of Samples | 100
indirect to direct field-related cost | 0.06539
FTEs Per Onsite Operator (24/7) | 5
FTEs Per Offsite Operator (24/7) | 5
FTEs Per Security Staff (24/7) | 5
Hours Per FTE | 1800
Work Hours Per Shift | 10
Maintenance to Direct Cost Ratio | 0.01
Onsite Learning | 0.08
No Learning | 0
Licensing Learning | 0
Factory Primary Structure | 0.18443
Factory Drums | 0.24138
Factory Other | 0.22963
Factory Be | 0.41505
Factory BeO | 0.39915
Non-nuclear off-the-shelf | 0.05
FTEs Per Operator Per Year Per Refueling | 0.0051852
Capacity Factor | 0.98904
Annual Electricity Production | 51984
FTEs Per Onsite Operator Per Year | 0.017037
Assumed Number Of Units For Onsite Learning | 200
No Learning Cost Multiplier | 1
Licensing Learning Cost Multiplier | 1
Factory Primary Structure Cost Multiplier | 0.25808
Factory Drums Cost Multiplier | 0.15955
Factory Other Cost Multiplier | 0.17671
Factory Be Cost Multiplier | 0.028363
Factory BeO Cost Multiplier | 0.033897
Non-nuclear off-the-shelf Cost Multiplier | 0.71121
Onsite Learning Cost Multiplier | 0.57466