## cost estimate
Account | Account Title | FOAK Estimated Cost ($2025) | NOAK Estimated Cost ($2025) | FOAK Estimated Cost std ($2025) | NOAK Estimated Cost std ($2025) | FOAK LCOE | NOAK LCOE | FOAK LCOE_std | NOAK LCOE_std
10 | Capitalized Pre-Construction Costs | 39611768 | 39611768 | 3930894 | 3930894 | 52 | 52 | 5 | 5
11 | Land Cost | 79715 | 79715 | 12117 | 12117 | 0 | 0 | 0 | 0
12 | Site Permits | 74226 | 74226 | 11700 | 11700 | 0 | 0 | 0 | 0
13 | Plant Licensing | 28305491 | 28305491 | 3529823 | 3529823 | 37 | 37 | 4 | 4
14 | Plant Permits | 5076773 | 5076773 | 1116873 | 1116873 | 6 | 6 | 1 | 1
15 | Plant Studies | 6075561 | 6075561 | 1450316 | 1450316 | 8 | 8 | 1 | 1
20 | Capitalized Direct Costs | 105587637 | 40617567 | 18698441 | 11268040 | 140 | 53 | 24 | 14
21 | Structures and Improvements | 15708418 | 3627381 | 8292494 | 1484700 | 20 | 4 | 10 | 1
211 | Site Preparation/ Yard Work | 201943 | 116048 | 22307 | 12819 | 0 | 0 | 0 | 0
211.1 | Cleaning and Grubbing | 117995 | 67807 | 19113 | 10984 | 0 | 0 | 0 | 0
211.2 | Stripping Topsoil | 69182 | 39756 | 10732 | 6167 | 0 | 0 | 0 | 0
211.3 | Excavation | 14765 | 8485 | 2259 | 1298 | 0 | 0 | 0 | 0
212 | Reactor Island Civil Structures | 1782701 | 1024448 | 419835 | 241262 | 2 | 1 | 0 | 0
212.1 | Reactor Building Slab Roof | 194803 | 111945 | 31643 | 18184 | 0 | 0 | 0 | 0
212.2 | Reactor Building Basement | 152821 | 87820 | 23596 | 13560 | 0 | 0 | 0 | 0
212.3 | Reactor Building Walls | 159161 | 91464 | 23619 | 13573 | 0 | 0 | 0 | 0
212.4 | Reactor Building Liner | 1114434 | 640421 | 407595 | 234229 | 1 | 0 | 0 | 0
212.5 | Reactor Building HVAC | 161480 | 92796 | 89518 | 51442 | 0 | 0 | 0 | 0
213 | Main Function Buildings | 76773 | 44118 | 5236 | 3008 | 0 | 0 | 0 | 0
213.1 | Energy conversion Building | 51270 | 29463 | 4839 | 2780 | 0 | 0 | 0 | 0
213.11 | Energy Conversion Building Slab Roof | 15780 | 9068 | 2371 | 1362 | 0 | 0 | 0 | 0
213.12 | Energy Conversion Building Basement | 12582 | 7230 | 1978 | 1137 | 0 | 0 | 0 | 0
213.13 | Energy Conversion Building Walls | 22907 | 13164 | 3620 | 2080 | 0 | 0 | 0 | 0
213.2 | Control building | 25502 | 14655 | 2286 | 1313 | 0 | 0 | 0 | 0
213.21 | Control Building Slab Roof | 7917 | 4550 | 1193 | 686 | 0 | 0 | 0 | 0
213.22 | Control Building Basement | 6161 | 3540 | 968 | 556 | 0 | 0 | 0 | 0
213.23 | Control Building Walls | 11423 | 6564 | 1754 | 1008 | 0 | 0 | 0 | 0
214 | Buildings to Support Main Function | 13606397 | 2419432 | 8278076 | 1462795 | 18 | 3 | 10 | 1
214.7 | Emergency and Start-up Power Systems Building | 13568470 | 2397636 | 8278065 | 1462788 | 17 | 3 | 10 | 1
214.72 | Diesel Generator | 13568470 | 2397636 | 8278065 | 1462788 | 17 | 3 | 10 | 1
214.8 | Auxilliary Building | 37927 | 21795 | 3815 | 2192 | 0 | 0 | 0 | 0
214.81 | Maniplator Building | 37927 | 21795 | 3815 | 2192 | 0 | 0 | 0 | 0
214.811 | Manipulator Building Slab Roof | 6327 | 3636 | 968 | 556 | 0 | 0 | 0 | 0
214.812 | ManipulatorBuilding Basement | 18812 | 10810 | 3044 | 1749 | 0 | 0 | 0 | 0
214.813 | Manipulator Building Exterior Walls | 12788 | 7348 | 2056 | 1181 | 0 | 0 | 0 | 0
215 | Supply Chain Buildings | 40603 | 23332 | 3720 | 2138 | 0 | 0 | 0 | 0
215.1 | Storage Building | 40603 | 23332 | 3720 | 2138 | 0 | 0 | 0 | 0
215.11 | Storage Building Slab Roof | 15652 | 8994 | 2398 | 1378 | 0 | 0 | 0 | 0
215.12 | Storage Building Basement | 12363 | 7104 | 1960 | 1126 | 0 | 0 | 0 | 0
215.13 | Storage Building Walls | 12587 | 7233 | 1973 | 1133 | 0 | 0 | 0 | 0
22 | Reactor System | 52786919 | 10673532 | 5545645 | 1008112 | 69 | 14 | 7 | 1
221 | Reactor Components | 38038000 | 7322743 | 4979234 | 906612 | 50 | 9 | 6 | 1
221.1 | Reactor Vessel and Accessories | 8813988 | 2274718 | 1222259 | 315441 | 11 | 3 | 1 | 0
221.11 | Reactor Support | 869052 | 224285 | 133346 | 34414 | 1 | 0 | 0 | 0
221.12 | Outer Vessel Structure - stainless_steel | 524753 | 135428 | 104801 | 27047 | 0 | 0 | 0 | 0
221.13 | Inner Vessel Structure - stainless_steel | 7420182 | 1915004 | 1208610 | 311918 | 9 | 2 | 1 | 0
221.2 | Reactor Control Devices | 7500656 | 1209366 | 760102 | 121568 | 9 | 1 | 1 | 0
221.21 | Reactivity Control System | 7500656 | 1209366 | 760102 | 121568 | 9 | 1 | 1 | 0
221.211 | Reactivity Control System Fabrication | 4673605 | 745676 | 718184 | 114586 | 6 | 0 | 0 | 0
221.212 | Installation | 1083697 | 172904 | 168504 | 26885 | 1 | 0 | 0 | 0
221.213 | Control Drums Materials (Absorber) - B4C_enriched | 691186 | 122137 | 109031 | 19266 | 0 | 0 | 0 | 0
221.214 | Control Drums Materials (Reflector) - Graphite | 45124 | 7973 | 7264 | 1283 | 0 | 0 | 0 | 0
221.215 | Control System Drive Mechanism | 1007041 | 160674 | 161739 | 25805 | 1 | 0 | 0 | 0
221.3 | Non-Fuel Core Internals | 21723356 | 3838658 | 4793601 | 847060 | 28 | 5 | 6 | 1
221.31 | Reflector | 49665 | 8776 | 5620 | 993 | 0 | 0 | 0 | 0
221.311 | Radial Reflector - Graphite | 27395 | 4840 | 4279 | 756 | 0 | 0 | 0 | 0
221.312 | Axial Reflector - Graphite | 22269 | 3935 | 3417 | 603 | 0 | 0 | 0 | 0
221.32 | Shield | 20887176 | 3690900 | 4793058 | 846964 | 27 | 4 | 6 | 1
221.321 | In Vessel Shield Materials - B4C_natural | 18833305 | 3327967 | 4786115 | 845737 | 24 | 4 | 6 | 1
221.322 | Out The Vessel Shield Materials - WEP | 40491 | 7155 | 6805 | 1202 | 0 | 0 | 0 | 0
221.323 | Isocontainer Steel Shell - carbon_steel - 1 | 2013379 | 355777 | 316616 | 55948 | 2 | 0 | 0 | 0
221.33 | Moderator - ZrH | 786514 | 138982 | 122118 | 21579 | 1 | 0 | 0 | 0
222 | Main Heat Transport System | 2911686 | 1259072 | 600078 | 176418 | 3 | 1 | 0 | 0
222.1 | Fluid Circulation Drive System | 1151266 | 203436 | 570182 | 100755 | 1 | 0 | 0 | 0
222.11 | Primary Pump - Yes | 1151266 | 203436 | 570182 | 100755 | 1 | 0 | 0 | 0
222.2 | Reactor Heat Transfer Piping System - LTMR | 193949 | 34272 | 30596 | 5406 | 0 | 0 | 0 | 0
222.3 | Heat Exchangers | 662104 | 116998 | 102081 | 18038 | 0 | 0 | 0 | 0
222.31 | Primary Heat Exchanger - SS316 | 662104 | 116998 | 102081 | 18038 | 0 | 0 | 0 | 0
222.5 | Initial Coolant Inventory - NaK | 904366 | 904366 | 142389 | 142389 | 1 | 1 | 0 | 0
223 | Safety Systems | 917710 | 162165 | 97671 | 17259 | 1 | 0 | 0 | 0
223.2 | Reactor Cavity Cooling System (Rvacs) | 917710 | 162165 | 97671 | 17259 | 1 | 0 | 0 | 0
223.21 | Rvacs (Cooling Vessel) | 445013 | 78636 | 69217 | 12231 | 0 | 0 | 0 | 0
223.22 | Rvacs (Intake Vessel) | 472696 | 83528 | 72999 | 12899 | 0 | 0 | 0 | 0
226 | Other Reactor Plant Equipment - LTMR | 538159 | 95096 | 118767 | 20986 | 0 | 0 | 0 | 0
227 | Reactor Instrumentation and Control (I&C) | 10345240 | 1828071 | 2330487 | 411812 | 13 | 2 | 3 | 0
228 | Reactor Plant Miscellaneous Items | 36121 | 6382 | 7957 | 1406 | 0 | 0 | 0 | 0
23 | Energy Conversion System | 20079251 | 13639292 | 14978480 | 10650884 | 26 | 18 | 19 | 14
232 | Energy Applications | 18879441 | 13427278 | 14975384 | 10650666 | 25 | 17 | 19 | 14
232.1 | Electricity Generation Systems | 18879441 | 13427278 | 14975384 | 10650666 | 25 | 17 | 19 | 14
236 | Common Instrumentation & Controls | 1199810 | 212014 | 272811 | 48207 | 1 | 0 | 0 | 0
24 | Electrical Equipment | 10784134 | 7669801 | 3423803 | 2435049 | 14 | 10 | 4 | 3
241 | Switchgear | 1011796 | 719601 | 581979 | 413910 | 1 | 0 | 0 | 0
242 | Station Service Equipment | 875108 | 622387 | 522804 | 371824 | 1 | 0 | 0 | 0
243 | Switchboards | 281391 | 200129 | 169123 | 120282 | 0 | 0 | 0 | 0
244 | Protective Equipment | 826036 | 587486 | 477806 | 339821 | 1 | 0 | 0 | 0
245 | Electrical Structure & Wiring Container | 4385559 | 3119060 | 2542955 | 1808579 | 5 | 4 | 3 | 2
246 | Power & Control Wiring | 3404241 | 2421136 | 2058264 | 1463861 | 4 | 3 | 2 | 1
25 | Initial Fuel Inventory | 4575783 | 4575783 | 857468 | 857468 | 6 | 6 | 1 | 1
251 | First Core Mining | 2846930 | 2846930 | 441282 | 441282 | 3 | 3 | 0 | 0
252 | First Core Conversion | 235020 | 235020 | 37695 | 37695 | 0 | 0 | 0 | 0
253 | First Core Enrichment | 1493832 | 1493832 | 732799 | 732799 | 1 | 1 | 0 | 0
26 | Miscellaneous Equipment (Cranes) | 1483497 | 262143 | 331827 | 58636 | 1 | 0 | 0 | 0
27 | Reactor Transportation to Site | 169632 | 169632 | 877 | 877 | 0 | 0 | 0 | 0
30 | Capitalized Indirect Services Cost | 12645149 | 5360329 | 2332833 | 1122961 | 16 | 7 | 3 | 1
31 | Factory & field indirect costs | 5791886 | 1827008 | 1195900 | 709431 | 7 | 2 | 1 | 0
32 | Factory and construction supervision | 1819278 | 640487 | 1281154 | 429051 | 2 | 0 | 1 | 0
33 | Startup Costs | 2836264 | 1629890 | 617646 | 354937 | 3 | 2 | 0 | 0
34 | Shipping and Transportation Costs | 983765 | 565331 | 218137 | 125354 | 1 | 0 | 0 | 0
35 | Engineering Services | 726005 | 417206 | 166994 | 95965 | 0 | 0 | 0 | 0
36 | PM/CM Services | 487949 | 280405 | 108785 | 62514 | 0 | 0 | 0 | 0
40 | Capitalized training costs | 352867 | 352867 | 78455 | 78455 | 0 | 0 | 0 | 0
41 | staff recruitment and training | 352867 | 352867 | 78455 | 78455 | 0 | 0 | 0 | 0
60 | Capitalized Financial Costs | 1820308 | 988903 | 243153 | 149388 | 2 | 1 | 0 | 0
62 | Interest | 1820308 | 988903 | 243153 | 149388 | 2 | 1 | 0 | 0
70 | Annualized O&M Cost | 8266409 | 4441134 | 712201 | 473727 | 153 | 82 | 13 | 8
71 | O&M Staff | 2361075 | 2361075 | 300751 | 300751 | 43 | 43 | 5 | 5
711 | Operators | 374412 | 374412 | 61679 | 61679 | 6 | 6 | 1 | 1
712 | Remote Monitoring Technicians - Autonomous | 119930 | 119930 | 26036 | 26036 | 2 | 2 | 0 | 0
713 | Security Staff | 1866732 | 1866732 | 295630 | 295630 | 34 | 34 | 5 | 5
72 | Variable Non-Fuel Costs | 206720 | 206720 | 157 | 157 | 3 | 3 | 0 | 0
722 | Reactor Return Transport | 206720 | 206720 | 157 | 157 | 3 | 3 | 0 | 0
73 | Regulatory Costs | 126175 | 126175 | 28038 | 28038 | 2 | 2 | 0 | 0
75 | Capital Plant Expenditures | 5504329 | 1709529 | 611685 | 342348 | 102 | 31 | 11 | 6
751 | Annualized RPV Replacements | 92994 | 23999 | 18572 | 4793 | 1 | 0 | 0 | 0
752 | Annualized Core Barrel Replacements | 1314967 | 339367 | 214183 | 55276 | 24 | 6 | 3 | 1
753 | Annualized Moderator Replacements | 139382 | 24629 | 21641 | 3824 | 2 | 0 | 0 | 0
754 | Annualized Reflector Replacements | 8801 | 1555 | 996 | 176 | 0 | 0 | 0 | 0
755 | Annualized Reactivity Control Replacements | 1329228 | 214317 | 134701 | 21543 | 24 | 3 | 2 | 0
759 | Annualized Misc. Replacements | 2618956 | 1105659 | 560089 | 338183 | 48 | 20 | 10 | 6
78 | Annualized Decommissioning Cost | 68107 | 37632 | 8986 | 5648 | 1 | 0 | 0 | 0
80 | Annualized Fuel Cost | 872605 | 872605 | 152354 | 152354 | 16 | 16 | 2 | 2
81 | Refueling Operations | 1938 | 1938 | 311 | 311 | 0 | 0 | 0 | 0
82 | Additional Nuclear Fuel | 810897 | 810897 | 151956 | 151956 | 15 | 15 | 2 | 2
83 | Spent Fuel Management | 59769 | 59769 | 9290 | 9290 | 1 | 1 | 0 | 0
OCC | Overnight Capital Cost | 158197422 | 85942532 | 21131706 | 12982855 | - | - | - | -
OCC per kW | Overnight Capital Cost per kW | 25515 | 13861 | 3408 | 2094 | - | - | - | -
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 153621639 | 81366749 | 21129027 | 12967306 | - | - | - | -
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 24777 | 13123 | 3407 | 2091 | - | - | - | -
TCI | Total Capital Investment | 160017730 | 86931435 | 21374859 | 13132243 | - | - | - | -
TCI per kW | Total Capital Investment per kW | 25809 | 14021 | 3447 | 2118 | - | - | - | -
AC | Annualized Cost | 9139015 | 5313739 | 735168 | 507458 | - | - | - | -
AC per MWh | Annualized Cost per MWh | 170 | 98 | 13 | 9 | - | - | - | -
LCOE | Levelized Cost Of Energy ($/MWh) | 382 | 214 | 40 | 24 | - | - | - | -
LCOH | Levelized Cost Of Heat ($/MWth) | 103 | 58 | 10 | 6 | - | - | - | -

## Parameters
Group | Parameter | Value | Units | Description | Source
--- SETTINGS ---
Settings | cross_sections_xml_location | /home/garcsamu/OpenMC/cross_sections/endfb-viii.1-hdf5/cross_sections.xml |  | File path to the OpenMC cross sections XML file on HPC | User Input
Settings | plotting | Y |  | Whether to generate and save geometry plots (Y = yes, N = no) | User Input
Settings | simplified_chain_thermal_xml | /home/garcsamu/OpenMC/TEMA/data/chain_casl_pwr.xml |  | File path to the simplified depletion chain XML file for thermal reactors | User Input
--- MATERIALS ---
Materials | Axial Reflector | Graphite |  | Axial reflector material type — may differ from radial reflector | User Input
Materials | Common Temperature | 600 | K | Uniform operating temperature applied to all materials in isothermal simulations | User Input
Materials | Control Drum Absorber | B4C_enriched |  | Neutron absorber material in the control drums (e.g. B4C_enriched, B4C_natural) | User Input
Materials | Control Drum Reflector | Graphite |  | Reflector material in the control drums (e.g. Graphite) | User Input
Materials | Coolant | NaK |  | Primary coolant material type (e.g. NaK, Helium) | User Input
Materials | Enrichment | 0.1975 | fraction | Uranium-235 enrichment fraction (0 to 1) | User Input
Materials | Fuel | UZrH_alloy |  | Primary fuel material type (e.g. TRIGA_fuel, UO2, UN, UC, homog_TRISO) | User Input
Materials | HX Material | SS316 |  | Heat exchanger structural material (e.g. SS316) | User Input
Materials | H_Zr_ratio | 1.6 | atomic ratio | Ratio of hydrogen atoms to zirconium atoms in TRIGA fuel (ZrH hydride) | User Input
Materials | Moderator | ZrH |  | Neutron moderator material type (e.g. ZrH, Graphite, monolith_graphite) | User Input
Materials | Radial Reflector | Graphite |  | Radial reflector material type (e.g. Graphite, BeO) | User Input
Materials | TRISO Fueled | No |  | Whether the reactor uses TRISO fuel particles (Yes or No) | User Input
Materials | UO2 atom fraction | 0.75 | fraction | Atom fraction of UO2 in the UCO mixed fuel (remainder is UC) | User Input
Materials | U_met_wo | 0.3 | weight fraction | Weight fraction of uranium metal in TRIGA fuel (remainder is ZrH matrix) | User Input
Materials | er_wo | 0 | weight fraction | Weight fraction of erbium burnable poison in TRIGA fuel (0 means no erbium) | User Input
Materials | reactor type | LTMR |  | Reactor type identifier: LTMR (liquid metal thermal), GCMR (gas-cooled), or HPMR (heat pipe) | User Input
--- GEOMETRY ---
Geometry | Active Height | 78.4 | cm | Axial height of the active fuel region | User Input
Geometry | Assembly FTF | 65.8006 | cm | Assembly flat-to-flat distance (distance between opposite parallel faces of the hexagonal assembly). | Calculated
Geometry | Axial Reflector Thickness | 19.2924 | cm | Thickness of each axial neutron reflector (top and bottom) | User Input
Geometry | Core Radius | 52.1927 | cm | Total core radius including the radial reflector | Calculated
Geometry | Fuel Pin Count | 300 |  | Total number of fuel pins (or fuel elements) in the entire core | Calculated
Geometry | Fuel Pin Materials | ['Zr', None, 'UZrH_alloy', None, 'SS304'] |  | Ordered list of materials for each fuel pin region from innermost to outermost | User Input
Geometry | Fuel Pin Radii | [0.28575, 0.3175, 1.5113, 1.5367, 1.5875] | cm | Ordered list of radii defining fuel pin region boundaries from innermost to outermost | User Input
Geometry | Lattice Apothem | 32.9003 | cm | Distance from the hex lattice center to the midpoint of a flat face of the outermost pin lattice. | Calculated
Geometry | Lattice Radius | 32.9003 | cm | Legacy LTMR name for the hex lattice apothem: distance from the hex lattice center to the midpoint of a flat face. | Calculated
Geometry | Moderator Pin Count | 97 |  | Total number of moderator pins in the entire core | Calculated
Geometry | Moderator Pin Inner Radius | 1.5367 | cm | Inner radius of the moderator pin cladding | User Input
Geometry | Moderator Pin Materials | ['ZrH', 'SS304'] |  | Ordered list of materials for each moderator pin region from innermost to outermost | User Input
Geometry | Moderator Pin Radii | [1.5367, 1.5875] | cm | Ordered list of radii defining moderator pin region boundaries | User Input
Geometry | Number of Rings per Assembly | 12 |  | Number of pin rings along the side of the hexagonal assembly (LTMR/HPMR) | User Input
Geometry | Pin Gap Distance | 0.1 | cm | Gap distance between adjacent pins (center-to-center minus two outer radii) | User Input
Geometry | Radial Reflector Thickness | 19.2924 | cm | Thickness of the radial neutron reflector surrounding the active core | User Input
--- CONTROL DRUMS ---
Control Drums | All Drums Area | 3064.4951 | cm² | Total cross-sectional area of all control drums | Calculated
Control Drums | All Drums Volume | 358499.3505 | cm³ | Total volume of all control drums combined | Calculated
Control Drums | Control Drum Absorber Mass | 63.0965 | kg | Total mass of absorber material in all control drums | Calculated
Control Drums | Control Drum Reflector Mass | 533.5377 | kg | Total mass of reflector material in all control drums | Calculated
Control Drums | Control Drums Mass | 596.6342 | kg | Total combined mass of all control drums (absorber + reflector) | Calculated
Control Drums | Drum Absorber Arc Degrees | 120 | degrees | Angular span of the absorber arc on each control drum | User Input
Control Drums | Drum Absorber Thickness | 1 | cm | Thickness of the absorber arc section within each control drum | User Input
Control Drums | Drum Count | 12 |  | Total number of control drums in the core | Calculated
Control Drums | Drum Height | 116.9848 | cm | Height of the control drums (typically active height + 2x axial reflector thickness) | User Input
Control Drums | Drum Radius | 9.016 | cm | Outer radius of each control drum. If not specified, it is automatically set to the largest allowable value that avoids drum overlap. | User Input
Control Drums | Number of Drums | 12 |  | Number of control drums in the core (e.g. 6, 12) | User Input
--- CORE DESIGN ---
Core Design | Axial Reflector Mass | 264.1653 | kg | Total mass of both axial reflectors (top and bottom combined) | Calculated
Core Design | Fuel Element Mass | 1284.3416 | kg | Total mass of the complete fuel elements (fuel meat + gap + cladding) across all fuel pins | Calculated
Core Design | Moderator Mass | 315.9395 | kg | Total mass of the neutron moderator material in the core | Calculated
Core Design | Radial Reflector Mass | 326.3974 | kg | Total mass of the radial neutron reflector | Calculated
--- OVERALL SYSTEM ---
Overall System | Burnup Steps | [0.1, 0.5, 160, 200] | MWd/kg | Cumulative burnup values at each depletion time step | User Input
Overall System | Heat Flux | 0.85251 | MW/m² | Calculated average fuel surface heat flux at full power | Calculated
Overall System | Heat Flux Criteria | 0.9 | MW/m² | Maximum allowable fuel surface heat flux (design constraint) | User Input
Overall System | Power MWe | 6.2 | MWe | Reactor net electric power output (thermal power × thermal efficiency) | Calculated
Overall System | Power MWt | 20 | MWt | Reactor thermal power output | User Input
Overall System | Thermal Efficiency | 0.31 | fraction | Net thermal-to-electric conversion efficiency of the power conversion system | User Input
--- OPENMC SETTINGS ---
OpenMC Settings | Cold Shutdown Temperature | 300 | K | Temperature used for the shutdown-state (ARI) keff calculation during shutdown margin evaluation. | User Input
OpenMC Settings | Isothermal Temperature Coefficients | FALSE |  | Whether isothermal temperature reactivity coefficients were calculated | User Input
OpenMC Settings | Particles | 1000 |  | Number of neutron histories per OpenMC batch | User Input
OpenMC Settings | Shutdown Margin Calc | FALSE |  | Whether shutdown margin is calculated. When True, the shutdown-state keff is evaluated with the absorber facing the core (ARI) at Cold Shutdown Temperature, and shutdown margin metrics are reported from ((1 - k_s) / k_s). | User Input
--- PHYSICS RESULTS ---
Physics Results | BOL Axial Non-Leakage Probability | 0.99084 | fraction | Beginning-of-life axial non-leakage probability from the 2D-to-3D buckling correction model. | Calculated
Physics Results | BOL Total Non-Leakage Probability | 0.9654 | fraction | Beginning-of-life total non-leakage probability from the axial-plus-radial buckling model. Returns NaN when Core Radius is not available. | Calculated
Physics Results | Depletion Time Steps | [0.0, 1.7274, 8.637, 2763.8471, 3454.8089] | days | Calculated cumulative depletion times corresponding to the reported keff values and used as the x-axis in keff_comparison_vs_Time.png. | Calculated
Physics Results | Estimated Axial Leakage (%) | 0.91645 | % | Estimated beginning-of-life axial neutron leakage percentage from the axial buckling correction model, computed as 100 × (1 - axial non-leakage probability). | Calculated
Physics Results | Estimated Total Leakage (%) | 3.4598 | % | Estimated beginning-of-life total neutron leakage percentage from the axial-plus-radial buckling model, computed as 100 × (1 - total non-leakage probability). Returns NaN when Core Radius is not available. | Calculated
Physics Results | Fuel Lifetime | 2702 | days | Estimated fuel cycle length — time for the 3D-corrected keff to fall to 1.0 | Calculated
Physics Results | Fuel Tail Waste Mass | 14299.9048 | kg | Mass of depleted uranium tails produced during the enrichment process | Calculated
Physics Results | Mass U235 | 67539.1073 | g | Initial mass of U-235 in the fresh fuel load | Calculated
Physics Results | Mass U238 | 277941.7848 | g | Initial mass of U-238 in the fresh fuel load | Calculated
Physics Results | Max Peaking Factor | 1.9765 | unitless | Maximum pin peaking factor across all depletion steps — the most limiting value over the fuel lifetime | Calculated
Physics Results | Max Peaking Factors per Step | [1.7833160875957783, 1.8283711514375665, 1.8836891415877899, 1.9571386893977551, 1.9764917037028513] | unitless | List of the maximum pin peaking factor at each depletion step, in step order | Calculated
Physics Results | Maximum Shutdown Margin 2D | N/A | pcm | Maximum shutdown margin from the 2D simulation, computed as max((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Maximum Shutdown Margin 3D (2D corrected) | N/A | pcm | Maximum shutdown margin corrected from 2D to 3D using axial neutron leakage correction, computed as max((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state corrected keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Most Limiting Shutdown Margin 2D | N/A | pcm | Most limiting shutdown margin from the 2D simulation, computed as min((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) | N/A | pcm | Most limiting shutdown margin corrected from 2D to 3D using axial neutron leakage correction, computed as min((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state corrected keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Natural Uranium Mass | 14645.3856 | kg | Mass of natural uranium feed required to produce the enriched fuel | Calculated
Physics Results | Region ID with Max Peaking Factor | 196 | unitless | Region ID with the highest peaking factor across all depletion steps; for LTMR this is typically a pin/distribcell ID, while for GCMR it is a mesh-region index | Calculated
Physics Results | SWU | 14197.4432 | kg-SWU | Separative work units required to produce the enriched fuel | Calculated
Physics Results | Step with Max Peaking Factor | 5 | unitless | Depletion step number at which the maximum peaking factor occurs | Calculated
Physics Results | Temp Coeff 2D | N/A | pcm/K | Most limiting (least negative) isothermal temperature coefficient from the 2D simulation. Negative values indicate self-stabilizing behavior. Note: 2D simulation overestimates keff — use 3D corrected value for safety conclusions. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) | N/A | pcm/K | Most limiting (least negative) isothermal temperature coefficient corrected from 2D to 3D using axial neutron leakage correction. Negative values confirm self-stabilizing behavior. Use this value for safety analysis. | Calculated
Physics Results | Uranium Mass | 345.4809 | kg | Total initial uranium mass in the fresh fuel load (U-235 + U-238) | Calculated
Physics Results | keff 2D | [1.3803860898361409, 1.3500599818069974, 1.3557559403798285, 1.0023217827682014, 0.865192175386941] |  | keff at each burnup step for the operating configuration (ARO) from the 2D OpenMC simulation, evaluated at Common Temperature. | Calculated
Physics Results | keff 3D (2D corrected) | [1.3677354943408397, 1.337907526137107, 1.343301985642931, 0.9921055470012373, 0.855480463624037] |  | keff at each burnup step for the operating configuration (ARO), corrected from 2D to 3D using axial leakage correction and evaluated at Common Temperature. | Calculated
--- PRIMARY LOOP & BALANCE OF PLANT ---
Primary Loop & Balance of Plant | BoP Count | 2 |  | Number of Balance of Plant (power conversion) systems | User Input
Primary Loop & Balance of Plant | BoP Power kWe | 3100 | kWe | Electric power handled by each BoP system | Calculated
Primary Loop & Balance of Plant | BoP per loop load fraction | 0.5 | fraction | Fraction of total electric load handled by each BoP system | User Input
Primary Loop & Balance of Plant | Coolant Mass Flow Rate | 226.2955 | kg/s | Total primary coolant mass flow rate | Calculated
Primary Loop & Balance of Plant | Primary HX Mass | 5208.2253 | kg | Calculated mass of the primary heat exchanger | Calculated
Primary Loop & Balance of Plant | Primary Loop Inlet Temperature | 703.15 | K | Primary coolant temperature at the core inlet | User Input
Primary Loop & Balance of Plant | Primary Loop Mass Flow Rate | 226.2955 | kg/s | Coolant mass flow rate per primary loop | Calculated
Primary Loop & Balance of Plant | Primary Loop Outlet Temperature | 793.15 | K | Primary coolant temperature at the core outlet | User Input
Primary Loop & Balance of Plant | Primary Pump | Yes |  | Whether a primary coolant pump is present (Yes or No) | User Input
Primary Loop & Balance of Plant | Primary Pump Mechanical Power | 94.2898 | kW | Mechanical power required to drive the primary coolant pump | Calculated
Primary Loop & Balance of Plant | Pump Isentropic Efficiency | 0.8 | fraction | Isentropic efficiency of the primary coolant pump | User Input
Primary Loop & Balance of Plant | Secondary HX Mass | 0 | kg | Mass of the secondary heat exchanger (0 if none) | User Input
Primary Loop & Balance of Plant | Secondary Loop Inlet Temperature | 668.15 | K | Secondary loop coolant temperature at the heat exchanger inlet | User Input
Primary Loop & Balance of Plant | Secondary Loop Outlet Temperature | 768.15 | K | Secondary loop coolant temperature at the heat exchanger outlet | User Input
Primary Loop & Balance of Plant | Secondary Pump | No |  | Whether a secondary coolant pump is present (Yes or No) | User Input
--- SHIELDING ---
Shielding | In Vessel Shield Inner Radius | 52.1927 | cm | Inner radius of the in-vessel radiation shield (equal to core radius) | User Input
Shielding | In Vessel Shield Mass | 1537.7246 | kg | Total mass of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Material | B4C_natural |  | Material of the in-vessel radiation shield | User Input
Shielding | In Vessel Shield Outer Radius | 62.3527 | cm | Outer radius of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Thickness | 10.16 | cm | Thickness of the in-vessel radiation shield (0 if none) | User Input
Shielding | Isocontainer Mass | 7942.3595 | kg | Total mass of the ISO container steel shell (mobile deployment only; 0 if stationary) | Calculated
Shielding | Out Of Vessel Shield Effective Density Factor | 0.5 | fraction | Effective density factor for the out-of-vessel shield — accounts for partial fill (e.g. 0.5 = 50% fill) | User Input
Shielding | Out Of Vessel Shield Mass | 1943.7074 | kg | Total mass of the out-of-vessel radiation shield | Calculated
Shielding | Out Of Vessel Shield Material | WEP |  | Material of the out-of-vessel radiation shield | User Input
Shielding | Out Of Vessel Shield Thickness | 30 | cm | Thickness of the out-of-vessel radiation shield | User Input
Shielding | Outer Shield Outer Radius | 103.8527 | cm | Outer radius of the out-of-vessel shield (outermost boundary of the shielded assembly) | Calculated
--- VESSELS ---
Vessels | Cooling Vessel Mass | 387.6647 | kg | Total mass of the cooling vessel | Calculated
Vessels | Cooling Vessel Material | stainless_steel |  | Structural material of the cooling vessel | User Input
Vessels | Cooling Vessel Radius | 70.3527 | cm | Outer radius of the cooling vessel | Calculated
Vessels | Cooling Vessel Thickness | 0.5 | cm | Wall thickness of the cooling vessel | User Input
Vessels | Gap Between Cooling Vessel And Intake Vessel | 3 | cm | Radial gap between the cooling vessel and intake vessel | User Input
Vessels | Gap Between Guard Vessel And Cooling Vessel | 5 | cm | Radial gap between the guard vessel and cooling vessel | User Input
Vessels | Gap Between Vessel And Guard Vessel | 2 | cm | Radial gap between the reactor vessel and guard vessel | User Input
Vessels | Guard Vessel Mass | 351.7088 | kg | Total mass of the guard vessel | Calculated
Vessels | Guard Vessel Material | stainless_steel |  | Structural material of the guard vessel | User Input
Vessels | Guard Vessel Radius | 65.3527 | cm | Outer radius of the guard vessel | Calculated
Vessels | Guard Vessel Thickness | 0.5 | cm | Wall thickness of the guard vessel (0 if none) | User Input
Vessels | Intake Vessel Mass | 410.106 | kg | Total mass of the intake vessel | Calculated
Vessels | Intake Vessel Material | stainless_steel |  | Structural material of the intake vessel | User Input
Vessels | Intake Vessel Radius | 73.3527 | cm | Outer radius of the intake vessel | Calculated
Vessels | Intake Vessel Thickness | 0.5 | cm | Wall thickness of the intake vessel | User Input
Vessels | Total Vessels Mass | 1813.6785 | kg | Combined mass of all vessel components (pressure vessel, guard, cooling, intake) | Calculated
Vessels | Vessel Bottom Depth | 32.129 | cm | Depth of the vessel bottom head (ellipsoidal) | User Input
Vessels | Vessel Height | 166.9848 | cm | Total height of the reactor pressure vessel | Calculated
Vessels | Vessel Lower Plenum Height | 2.848 | cm | Height of the lower plenum region below the active core | User Input
Vessels | Vessel Mass | 664.199 | kg | Total mass of the reactor pressure vessel | Calculated
Vessels | Vessel Material | stainless_steel |  | Structural material of the reactor pressure vessel | User Input
Vessels | Vessel Radius | 62.3527 | cm | Inner radius of the reactor pressure vessel (or core barrel) | User Input
Vessels | Vessel Thickness | 1 | cm | Wall thickness of the reactor pressure vessel | User Input
Vessels | Vessel Upper Gas Gap | 0 | cm | Height of the upper gas gap above the upper plenum (0 if none) | User Input
Vessels | Vessel Upper Plenum Height | 47.152 | cm | Height of the upper plenum region above the active core | User Input
Vessels | Vessels Total Height | 211.1138 | cm | Total height of the complete vessel assembly | Calculated
Vessels | Vessels Total Radius | 73.8527 | cm | Total outer radius of the complete vessel assembly | Calculated
--- OPERATION ---
Operation | A75: Core Barrel Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled core barrel replacements | User Input
Operation | A75: Drum Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled control drum replacements | User Input
Operation | A75: Reflector Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled reflector replacements | User Input
Operation | A75: Vessel Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled reactor pressure vessel replacements | User Input
Operation | A78: CAPEX to Decommissioning Cost Ratio | 0.15 | fraction | Ratio of total decommissioning cost to total capital cost (typical range: 9%–15%) | User Input
Operation | Annual Electricity Production | 53716.8 | MWh/year | Total annual electricity production at the calculated capacity factor | Calculated
Operation | Capacity Factor | 0.98904 | fraction | Annual plant capacity factor — fraction of the year the plant operates at full power | Calculated
Operation | Emergency Shutdowns Per Year | 0.2 | events/year | Expected number of unplanned emergency shutdowns per year | User Input
Operation | Levelization Period | 60 | years | Plant lifetime used for LCOE levelization (economic analysis period) | User Input
Operation | Maintenance to Direct Cost Ratio | 0.03 | fraction | Ratio of annual non-replacement maintenance cost to total direct capital cost | User Input
Operation | Number of Operators | 2 |  | Number of operators assigned per shift | User Input
Operation | Onsite Coolant Inventory | 7045.371 | kg | Total mass of coolant stored on site (fresh + used tanks) | User Input
Operation | Operation Mode | Autonomous |  | Reactor operation mode: Remotely Monitored or On-Site Staffed | User Input
Operation | Reactors Monitored Per Operator | 10 |  | Number of reactors that can be monitored by a single operator | User Input
Operation | Refueling Period | 7 | days | Duration of the scheduled refueling outage | User Input
Operation | Replacement Coolant Inventory | 0 | kg | Mass of coolant replaced per refueling cycle | User Input
Operation | Security Staff Per Shift | 2 |  | Number of security personnel required per shift | User Input
Operation | Startup Duration after Emergency Shutdown | 14 | days | Duration of the startup sequence following an emergency shutdown | User Input
Operation | Startup Duration after Refueling | 2 | days | Duration of the startup sequence following a refueling outage | User Input
--- ECONOMIC PARAMETERS ---
Economic Parameters | Annual Reactor Return Frequency | 0.125 | 1/year | Expected number of activated-unit return trips per year; set to 0 to disable account 722 | User Input
Economic Parameters | Annual Return | 0.0475 | fraction | Annual return rate assumed for the decommissioning reserve fund | User Input
Economic Parameters | Assumed Number Of Units For Onsite Learning | 200 |  | Number of units assumed for onsite learning (typically 2 × NOAK Unit Number) | Calculated
Economic Parameters | Construction Duration | 12 | months | Duration of plant construction used for financing cost calculation | User Input
Economic Parameters | Control Building Basement Volume | 5.9448 | m³ | Volume of concrete in the control building basement | User Input
Economic Parameters | Control Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the control building exterior walls | User Input
Economic Parameters | Control Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the control building slab roof | User Input
Economic Parameters | Debt To Equity Ratio | 0.5 | fraction | Ratio of debt financing to equity financing for the project | User Input
Economic Parameters | Deployment Mode | Mobile |  | Transport configuration: Mobile (fueled unit in one load), Semi-Mobile (unfueled reactor + fuel separately), or Stationary (core, shielding, fuel all separate) | User Input
Economic Parameters | Discount Rate | 0.07 | fraction | Annual discount rate (WACC) used for LCOE levelization and cost annualization | User Input
Economic Parameters | Emergency Building Basement Volume | 0 | m³ | Volume of concrete in the emergency building basement (0 if none) | User Input
Economic Parameters | Emergency Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the emergency building exterior walls (0 if none) | User Input
Economic Parameters | Emergency Building Slab Roof Volume | 0 | m³ | Volume of concrete in the emergency building slab roof (0 if none) | User Input
Economic Parameters | Enrichment Category | HALEU |  | LEU or HALEU, set from Enrichment during account 253 costing | Calculated
Economic Parameters | Escalation Year | 2025 | year | Reference year to which all costs are escalated for consistent comparison | User Input
Economic Parameters | Excavation Volume | 412.605 | m³ | Volume of earth to be excavated for plant construction | User Input
Economic Parameters | FTEs Per Offsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per offsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per onsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator Per Year | 1 | FTE/operator/year | Total FTE-years per operator per year including all activities | Calculated
Economic Parameters | FTEs Per Operator Per Year Per Refueling | 0.0051852 | FTE/operator/year | Fraction of an FTE spent per operator per year on refueling-related activities | User Input
Economic Parameters | FTEs Per Security Staff (24/7) | 5 | FTE/staff | Full-time equivalents needed per security staff position to maintain 24/7 coverage | User Input
Economic Parameters | Hours Per FTE | 1800 | hours/year | Annual working hours per full-time equivalent employee | User Input
Economic Parameters | Integrated Heat Exchanger Building Basement Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building basement (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building exterior walls (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Slab Roof Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building slab roof (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Superstructure Area | 0 | m² | Floor area of the integrated heat exchanger building superstructure (0 if none) | User Input
Economic Parameters | Interest Rate | 0.07 | fraction | Annual cost of debt used to calculate interest during construction (Account 62) | User Input
Economic Parameters | Land Area | 18 | acres | Total land area required for the plant site | User Input
Economic Parameters | Manipulator Building Basement Volume | 17.8374 | m³ | Volume of concrete in the manipulator building basement | User Input
Economic Parameters | Manipulator Building Exterior Walls Volume | 15.9195 | m³ | Volume of concrete in the manipulator building exterior walls | User Input
Economic Parameters | Manipulator Building Slab Roof Volume | 4.7566 | m³ | Volume of concrete in the manipulator building slab roof | User Input
Economic Parameters | NOAK Unit Number | 100 |  | Nth-of-a-kind unit number used to calculate the learning curve cost multiplier | User Input
Economic Parameters | Number of Samples | 1000 |  | Number of Monte Carlo samples used for cost uncertainty quantification | User Input
Economic Parameters | Radwaste Building Basement Volume | 0 | m³ | Volume of concrete in the radioactive waste building basement (0 if none) | User Input
Economic Parameters | Radwaste Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the radioactive waste building exterior walls (0 if none) | User Input
Economic Parameters | Radwaste Building Slab Roof Volume | 0 | m³ | Volume of concrete in the radioactive waste building slab roof (0 if none) | User Input
Economic Parameters | Reactor Building Basement Volume | 95.0976 | m³ | Volume of concrete in the reactor building basement | User Input
Economic Parameters | Reactor Building Exterior Walls Volume | 129.9564 | m³ | Volume of concrete in the reactor building exterior walls | User Input
Economic Parameters | Reactor Building Slab Roof Volume | 95.0976 | m³ | Volume of concrete in the reactor building slab roof | User Input
Economic Parameters | Reactor Building Superstructure Area | 77 | m² | Floor area of the reactor building superstructure | User Input
Economic Parameters | Refueling Building Basement Volume | 0 | m³ | Volume of concrete in the refueling building basement (0 if none) | User Input
Economic Parameters | Refueling Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the refueling building exterior walls (0 if none) | User Input
Economic Parameters | Refueling Building Slab Roof Volume | 0 | m³ | Volume of concrete in the refueling building slab roof (0 if none) | User Input
Economic Parameters | Spent Fuel Building Basement Volume | 0 | m³ | Volume of concrete in the spent fuel building basement (0 if none) | User Input
Economic Parameters | Spent Fuel Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the spent fuel building exterior walls (0 if none) | User Input
Economic Parameters | Spent Fuel Building Slab Roof Volume | 0 | m³ | Volume of concrete in the spent fuel building slab roof (0 if none) | User Input
Economic Parameters | Storage Building Basement Volume | 11.76 | m³ | Volume of concrete in the storage building basement | User Input
Economic Parameters | Storage Building Exterior Walls Volume | 15.768 | m³ | Volume of concrete in the storage building exterior walls | User Input
Economic Parameters | Storage Building Slab Roof Volume | 11.76 | m³ | Volume of concrete in the storage building slab roof (houses operational spares) | User Input
Economic Parameters | Transport Distance | 500 | miles | One-way road distance for reactor transport; set to 0 to disable transport accounts 27 and 722 | User Input
Economic Parameters | Transport Security Category | II |  | II, III, or Exempt, derived from enrichment and U-235 mass during account 27 costing | Calculated
Economic Parameters | Turbine Building Basement Volume | 5.9448 | m³ | Volume of concrete in the turbine building basement | User Input
Economic Parameters | Turbine Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the turbine building exterior walls | User Input
Economic Parameters | Turbine Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the turbine building slab roof | User Input
Economic Parameters | Work Hours Per Shift | 10 | hours | Duration of each work shift | User Input
Economic Parameters | indirect to direct field-related cost | 0.06539 | fraction | Ratio of indirect field (site) costs to total direct field costs — covers site supervision, temporary facilities, and other indirect site activities | User Input
--- LEARNING RATES ---
Learning Rates | Factory Be | 0.41505 | fraction | Learning rate for factory-manufactured beryllium components | User Input
Learning Rates | Factory Be Cost Multiplier | 0.028363 | fraction | NOAK cost multiplier for beryllium components based on Wright's Law | Calculated
Learning Rates | Factory BeO | 0.39915 | fraction | Learning rate for factory-manufactured beryllium oxide components | User Input
Learning Rates | Factory BeO Cost Multiplier | 0.033897 | fraction | NOAK cost multiplier for beryllium oxide components based on Wright's Law | Calculated
Learning Rates | Factory Drums | 0.24138 | fraction | Learning rate for factory-manufactured control drum components | User Input
Learning Rates | Factory Drums Cost Multiplier | 0.15955 | fraction | NOAK cost multiplier for factory-built control drums based on Wright's Law | Calculated
Learning Rates | Factory Other | 0.22963 | fraction | Learning rate for other factory-manufactured components | User Input
Learning Rates | Factory Other Cost Multiplier | 0.17671 | fraction | NOAK cost multiplier for other factory-built components based on Wright's Law | Calculated
Learning Rates | Factory Primary Structure | 0.18443 | fraction | Learning rate for factory-manufactured primary structural components | User Input
Learning Rates | Factory Primary Structure Cost Multiplier | 0.25808 | fraction | NOAK cost multiplier for factory-built primary structure based on Wright's Law | Calculated
Learning Rates | Licensing Learning | 0 | fraction | Learning rate for licensing costs per doubling of cumulative units produced | User Input
Learning Rates | Licensing Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for licensing costs based on Wright's Law | Calculated
Learning Rates | No Learning | 0 | fraction | Learning rate for components with no learning benefit (fixed costs, rate = 0) | User Input
Learning Rates | No Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for components with no learning (always 1.0) | Calculated
Learning Rates | Non-nuclear off-the-shelf | 0.05 | fraction | Learning rate for non-nuclear commercial off-the-shelf components | User Input
Learning Rates | Non-nuclear off-the-shelf Cost Multiplier | 0.71121 | fraction | NOAK cost multiplier for non-nuclear commercial components based on Wright's Law | Calculated
Learning Rates | Onsite Learning | 0.08 | fraction | Learning rate for onsite construction and installation activities | User Input
Learning Rates | Onsite Learning Cost Multiplier | 0.57466 | fraction | NOAK cost multiplier for onsite construction activities based on Wright's Law | Calculated
--- DEBUG / INTERMEDIATE VALUES ---
Debug / Intermediate Values | keff 2D ARO (BOL) | 1.3804 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — beginning of life | Calculated
Debug / Intermediate Values | keff 2D ARO (EOL) | 0.86519 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — end of life | Calculated
Debug / Intermediate Values | keff 2D ARO (min) | 0.86519 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 2D ARO (max) | 1.3804 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (BOL) | 1.3677 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (EOL) | 0.85548 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (min) | 0.85548 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (max) | 1.3677 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — maximum value | Calculated
--- UNCATEGORIZED ---
Uncategorized | Air Margin | 200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Cost_Data | /home/garcsamu/OpenMC/MOUSE/cost/Cost_Database.xlsx |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Evaluation Radii cm | {'iso_surface': 106.35270663989716, '1m_standoff': 206.35270663989718, '30m_exclusion': 3000} |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate 1m_standoff mSv_hr | 6.1113 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate 1m_standoff unc mSv_hr | 0.8608 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate 30m_exclusion mSv_hr | 0.028914 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate 30m_exclusion unc mSv_hr | 0.0040727 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate Limit Workers mSv_hr | 2.5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate Limit mSv_hr | 0.02 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface mSv_hr | 23.0067 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface neutron mSv_hr | 0.18141 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface photon mSv_hr | 22.8253 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface unc mSv_hr | 3.2406 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_ground mSv_hr | 10.8996 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_ground neutron mSv_hr | 0 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_ground photon mSv_hr | 10.8996 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_ground unc mSv_hr | 6.6327 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_lateral mSv_hr | 5.1395 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_lateral neutron mSv_hr | 0 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_lateral photon mSv_hr | 5.1395 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_lateral unc mSv_hr | 3.8125 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_sky mSv_hr | 7.6743 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_sky neutron mSv_hr | 0 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_sky photon mSv_hr | 7.6743 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dose Rate iso_surface_sky unc mSv_hr | 6.7695 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Fission Source File | /home/garcsamu/OpenMC/MOUSE/bol_fission_source.h5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Inner Radius | 104.8527 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Interior Height | 239 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Interior Length | 589 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Interior Width | 235 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Outer Radius | 106.3527 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Steel Material | carbon_steel |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Isocontainer Steel Thickness | 1.5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Mainenance to Direct Cost Ratio | 0.015 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Meets Public Limit | FALSE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Meets Worker Limit | FALSE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Mobile | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Out Of Vessel Shield Inner Radius | 74.8527 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Out Of Vessel Shield Outer Radius | 104.8527 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Outer Shield Inner Radius | 73.8527 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | PF Per Step | {1: Region_ID Peaking_Factor Step 0 0 0.527557 1 1 1 0.652210 1 2 2 0.704664 1 3 3 0.869750 1 4 4 0.927084 1 .. ... ... ... 295 295 0.781488 1 296 296 0.736157 1 297 297 0.730696 1 298 298 0.516396 1 299 299 0.499547 1 [300 rows x 3 columns], 2: Region_ID Peaking_Factor Step 0 0 0.553882 2 1 1 0.516900 2 2 2 0.800202 2 3 3 0.904077 2 4 4 0.929748 2 .. ... ... ... 295 295 0.546519 2 296 296 0.587961 2 297 297 0.555257 2 298 298 0.611624 2 299 299 0.463213 2 [300 rows x 3 columns], 3: Region_ID Peaking_Factor Step 0 0 0.526699 3 1 1 0.603306 3 2 2 0.697329 3 3 3 0.746958 3 4 4 0.730909 3 .. ... ... ... 295 295 0.744091 3 296 296 0.770645 3 297 297 0.695109 3 298 298 0.682844 3 299 299 0.553048 3 [300 rows x 3 columns], 4: Region_ID Peaking_Factor Step 0 0 0.608271 4 1 1 0.565858 4 2 2 0.781687 4 3 3 0.826368 4 4 4 0.900352 4 .. ... ... ... 295 295 0.814528 4 296 296 0.897498 4 297 297 0.693099 4 298 298 0.602311 4 299 299 0.479653 4 [300 rows x 3 columns], 5: Region_ID Peaking_Factor Step 0 0 0.543408 5 1 1 0.466350 5 2 2 0.621128 5 3 3 0.647387 5 4 4 0.537356 5 .. ... ... ... 295 295 0.840063 5 296 296 0.876848 5 297 297 0.711766 5 298 298 0.706704 5 299 299 0.762782 5 [300 rows x 3 columns]} |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Photon Transport | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SD Margin Calc | FALSE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Save Dose Map | FALSE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Batches | 50 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Ground Clearance | 100 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Inactive | 0 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Particles | 2000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Run | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Soil Depth | 200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Transport Heaviest Load (kg) | 16024.948 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Transport Loads (kg) | {'Full unit (core + shield + fuel)': 16024.947993165244} |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Transport Mass Limit (kg) | 22200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Within Transport Limit | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | XS_type | endf8.1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | shielding_output_dir | /home/garcsamu/OpenMC/MOUSE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown