## cost estimate
Account | Account Title | FOAK Estimated Cost ($2025) | NOAK Estimated Cost ($2025) | FOAK Estimated Cost std ($2025) | NOAK Estimated Cost std ($2025) | FOAK LCOE | NOAK LCOE | FOAK LCOE_std | NOAK LCOE_std
10 | Capitalized Pre-Construction Costs | 39546453 | 39546453 | 4047718 | 4047718 | 52 | 52 | 5 | 5
11 | Land Cost | 79239 | 79239 | 12351 | 12351 | 0 | 0 | 0 | 0
12 | Site Permits | 74033 | 74033 | 11590 | 11590 | 0 | 0 | 0 | 0
13 | Plant Licensing | 28124465 | 28124465 | 3542288 | 3542288 | 37 | 37 | 4 | 4
14 | Plant Permits | 5082159 | 5082159 | 1123155 | 1123155 | 6 | 6 | 1 | 1
15 | Plant Studies | 6186556 | 6186556 | 1377497 | 1377497 | 8 | 8 | 1 | 1
20 | Capitalized Direct Costs | 111495942 | 44816393 | 18092730 | 10882606 | 147 | 59 | 24 | 14
21 | Structures and Improvements | 15931009 | 3665283 | 8268174 | 1477940 | 21 | 4 | 10 | 1
211 | Site Preparation/ Yard Work | 201958 | 116057 | 21369 | 12280 | 0 | 0 | 0 | 0
211.1 | Cleaning and Grubbing | 119150 | 68470 | 18110 | 10407 | 0 | 0 | 0 | 0
211.2 | Stripping Topsoil | 68141 | 39158 | 10283 | 5909 | 0 | 0 | 0 | 0
211.3 | Excavation | 14666 | 8428 | 2189 | 1258 | 0 | 0 | 0 | 0
212 | Reactor Island Civil Structures | 1778853 | 1022237 | 423939 | 243621 | 2 | 1 | 0 | 0
212.1 | Reactor Building Slab Roof | 193141 | 110990 | 30000 | 17240 | 0 | 0 | 0 | 0
212.2 | Reactor Building Basement | 152332 | 87539 | 23751 | 13649 | 0 | 0 | 0 | 0
212.3 | Reactor Building Walls | 158706 | 91202 | 24987 | 14359 | 0 | 0 | 0 | 0
212.4 | Reactor Building Liner | 1112663 | 639403 | 412030 | 236777 | 1 | 0 | 0 | 0
212.5 | Reactor Building HVAC | 162009 | 93100 | 91282 | 52456 | 0 | 0 | 0 | 0
213 | Main Function Buildings | 76749 | 44105 | 5152 | 2960 | 0 | 0 | 0 | 0
213.1 | Energy conversion Building | 51109 | 29370 | 4669 | 2683 | 0 | 0 | 0 | 0
213.11 | Energy Conversion Building Slab Roof | 15800 | 9079 | 2435 | 1399 | 0 | 0 | 0 | 0
213.12 | Energy Conversion Building Basement | 12495 | 7180 | 1969 | 1131 | 0 | 0 | 0 | 0
213.13 | Energy Conversion Building Walls | 22813 | 13109 | 3512 | 2018 | 0 | 0 | 0 | 0
213.2 | Control building | 25640 | 14734 | 2355 | 1353 | 0 | 0 | 0 | 0
213.21 | Control Building Slab Roof | 7967 | 4578 | 1218 | 699 | 0 | 0 | 0 | 0
213.22 | Control Building Basement | 6223 | 3576 | 967 | 555 | 0 | 0 | 0 | 0
213.23 | Control Building Walls | 11449 | 6579 | 1857 | 1067 | 0 | 0 | 0 | 0
214 | Buildings to Support Main Function | 13832698 | 2459465 | 8260868 | 1459734 | 18 | 3 | 10 | 1
214.7 | Emergency and Start-up Power Systems Building | 13794659 | 2437606 | 8260907 | 1459756 | 18 | 3 | 10 | 1
214.72 | Diesel Generator | 13794659 | 2437606 | 8260907 | 1459756 | 18 | 3 | 10 | 1
214.8 | Auxilliary Building | 38039 | 21859 | 3718 | 2136 | 0 | 0 | 0 | 0
214.81 | Maniplator Building | 38039 | 21859 | 3718 | 2136 | 0 | 0 | 0 | 0
214.811 | Manipulator Building Slab Roof | 6358 | 3653 | 1018 | 585 | 0 | 0 | 0 | 0
214.812 | ManipulatorBuilding Basement | 18814 | 10812 | 2987 | 1716 | 0 | 0 | 0 | 0
214.813 | Manipulator Building Exterior Walls | 12866 | 7393 | 2039 | 1171 | 0 | 0 | 0 | 0
215 | Supply Chain Buildings | 40749 | 23417 | 3594 | 2065 | 0 | 0 | 0 | 0
215.1 | Storage Building | 40749 | 23417 | 3594 | 2065 | 0 | 0 | 0 | 0
215.11 | Storage Building Slab Roof | 15766 | 9060 | 2418 | 1390 | 0 | 0 | 0 | 0
215.12 | Storage Building Basement | 12374 | 7110 | 1943 | 1116 | 0 | 0 | 0 | 0
215.13 | Storage Building Walls | 12608 | 7245 | 1898 | 1091 | 0 | 0 | 0 | 0
22 | Reactor System | 58956135 | 15140226 | 6298477 | 1381313 | 78 | 20 | 8 | 1
221 | Reactor Components | 40354267 | 7952474 | 5623831 | 1023711 | 53 | 10 | 7 | 1
221.1 | Reactor Vessel and Accessories | 11513803 | 2971488 | 1330164 | 343289 | 15 | 3 | 1 | 0
221.11 | Reactor Support | 1386000 | 357699 | 211382 | 54553 | 1 | 0 | 0 | 0
221.12 | Outer Vessel Structure - stainless_steel | 1055701 | 272455 | 172035 | 44398 | 1 | 0 | 0 | 0
221.13 | Inner Vessel Structure - stainless_steel | 9072102 | 2341332 | 1320762 | 340863 | 12 | 3 | 1 | 0
221.2 | Reactor Control Devices | 7413944 | 1194781 | 750169 | 119901 | 9 | 1 | 0 | 0
221.21 | Reactivity Control System | 7413944 | 1194781 | 750169 | 119901 | 9 | 1 | 0 | 0
221.211 | Reactivity Control System Fabrication | 4624600 | 737858 | 703789 | 112290 | 6 | 0 | 0 | 0
221.212 | Installation | 1088707 | 173703 | 166445 | 26556 | 1 | 0 | 0 | 0
221.213 | Control Drums Materials (Absorber) - B4C_enriched | 648430 | 114581 | 97466 | 17222 | 0 | 0 | 0 | 0
221.214 | Control Drums Materials (Reflector) - Graphite | 44123 | 7796 | 6935 | 1225 | 0 | 0 | 0 | 0
221.215 | Control System Drive Mechanism | 1008081 | 160840 | 160734 | 25645 | 1 | 0 | 0 | 0
221.3 | Non-Fuel Core Internals | 21426519 | 3786205 | 5398228 | 953902 | 28 | 5 | 7 | 1
221.31 | Reflector | 10656 | 1883 | 2112 | 373 | 0 | 0 | 0 | 0
221.311 | Radial Reflector - Graphite | -2398 | -423 | 384 | 67 | 0 | 0 | 0 | 0
221.312 | Axial Reflector - Graphite | 13055 | 2307 | 2073 | 366 | 0 | 0 | 0 | 0
221.32 | Shield | 20633174 | 3646016 | 5397838 | 953833 | 27 | 4 | 7 | 1
221.321 | In Vessel Shield Materials - B4C_natural | 20568245 | 3634542 | 5398237 | 953903 | 27 | 4 | 7 | 1
221.322 | Out The Vessel Shield Materials - WEP | 64928 | 11473 | 11066 | 1955 | 0 | 0 | 0 | 0
221.33 | Moderator - ZrH | 782688 | 138306 | 125025 | 22092 | 1 | 0 | 0 | 0
222 | Main Heat Transport System | 6722156 | 5088529 | 940993 | 749242 | 8 | 6 | 1 | 0
222.1 | Fluid Circulation Drive System | 1129980 | 199674 | 578568 | 102236 | 1 | 0 | 0 | 0
222.11 | Primary Pump - Yes | 1129980 | 199674 | 578568 | 102236 | 1 | 0 | 0 | 0
222.2 | Reactor Heat Transfer Piping System - LTMR | 194757 | 34414 | 30322 | 5358 | 0 | 0 | 0 | 0
222.3 | Heat Exchangers | 659520 | 116541 | 98526 | 17410 | 0 | 0 | 0 | 0
222.31 | Primary Heat Exchanger - SS316 | 659520 | 116541 | 98526 | 17410 | 0 | 0 | 0 | 0
222.5 | Initial Coolant Inventory - NaK | 4737898 | 4737898 | 743149 | 743149 | 6 | 6 | 0 | 0
223 | Safety Systems | 1088583 | 192359 | 121749 | 21513 | 1 | 0 | 0 | 0
223.2 | Reactor Cavity Cooling System (Rvacs) | 1088583 | 192359 | 121749 | 21513 | 1 | 0 | 0 | 0
223.21 | Rvacs (Cooling Vessel) | 516924 | 91343 | 79666 | 14077 | 0 | 0 | 0 | 0
223.22 | Rvacs (Intake Vessel) | 571658 | 101015 | 92071 | 16269 | 0 | 0 | 0 | 0
226 | Other Reactor Plant Equipment - LTMR | 547497 | 96746 | 119804 | 21170 | 0 | 0 | 0 | 0
227 | Reactor Instrumentation and Control (I&C) | 10207011 | 1803645 | 2329247 | 411593 | 13 | 2 | 3 | 0
228 | Reactor Plant Miscellaneous Items | 36619 | 6470 | 8189 | 1447 | 0 | 0 | 0 | 0
23 | Energy Conversion System | 19640467 | 13335682 | 14503354 | 10314950 | 26 | 17 | 19 | 13
232 | Energy Applications | 18456482 | 13126464 | 14503951 | 10315378 | 24 | 17 | 19 | 13
232.1 | Electricity Generation Systems | 18456482 | 13126464 | 14503951 | 10315378 | 24 | 17 | 19 | 13
236 | Common Instrumentation & Controls | 1183985 | 209217 | 265754 | 46960 | 1 | 0 | 0 | 0
24 | Electrical Equipment | 10690328 | 7603085 | 3629850 | 2581591 | 14 | 10 | 4 | 3
241 | Switchgear | 1066491 | 758500 | 620704 | 441452 | 1 | 1 | 0 | 0
242 | Station Service Equipment | 889115 | 632349 | 546219 | 388477 | 1 | 0 | 0 | 0
243 | Switchboards | 282279 | 200760 | 162032 | 115239 | 0 | 0 | 0 | 0
244 | Protective Equipment | 835589 | 594281 | 497093 | 353538 | 1 | 0 | 0 | 0
245 | Electrical Structure & Wiring Container | 4367909 | 3106507 | 2856810 | 2031796 | 5 | 4 | 3 | 2
246 | Power & Control Wiring | 3248943 | 2310686 | 1866469 | 1327454 | 4 | 3 | 2 | 1
25 | Initial Fuel Inventory | 4813291 | 4813291 | 957262 | 957262 | 6 | 6 | 1 | 1
251 | First Core Mining | 2866668 | 2866668 | 443939 | 443939 | 3 | 3 | 0 | 0
252 | First Core Conversion | 232324 | 232324 | 35627 | 35627 | 0 | 0 | 0 | 0
253 | First Core Enrichment | 1714298 | 1714298 | 848749 | 848749 | 2 | 2 | 1 | 1
26 | Miscellaneous Equipment (Cranes) | 1464709 | 258823 | 322966 | 57070 | 1 | 0 | 0 | 0
30 | Capitalized Indirect Services Cost | 13046229 | 5559164 | 2214508 | 1007212 | 17 | 7 | 2 | 1
31 | Factory & field indirect costs | 6181154 | 2101710 | 1146618 | 681776 | 8 | 2 | 1 | 0
32 | Factory and construction supervision | 1757982 | 522608 | 1201011 | 313159 | 2 | 0 | 1 | 0
33 | Startup Costs | 2889007 | 1660199 | 651818 | 374574 | 3 | 2 | 0 | 0
34 | Shipping and Transportation Costs | 992522 | 570363 | 216109 | 124189 | 1 | 0 | 0 | 0
35 | Engineering Services | 729254 | 419073 | 164109 | 94307 | 0 | 0 | 0 | 0
36 | PM/CM Services | 496307 | 285208 | 112222 | 64489 | 0 | 0 | 0 | 0
40 | Capitalized training costs | 351894 | 351894 | 75407 | 75407 | 0 | 0 | 0 | 0
41 | staff recruitment and training | 351894 | 351894 | 75407 | 75407 | 0 | 0 | 0 | 0
60 | Capitalized Financial Costs | 2838217 | 1558113 | 352947 | 213475 | 3 | 2 | 0 | 0
62 | Interest | 2838217 | 1558113 | 352947 | 213475 | 3 | 2 | 0 | 0
70 | Annualized O&M Cost | 7658762 | 3274185 | 634152 | 368930 | 142 | 60 | 11 | 6
71 | O&M Staff | 1114885 | 1114885 | 158669 | 158669 | 20 | 20 | 2 | 2
711 | Operators | 6438 | 6438 | 1029 | 1029 | 0 | 0 | 0 | 0
712 | Remote Monitoring Technicians - Remotely Monitored | 120939 | 120939 | 27385 | 27385 | 2 | 2 | 0 | 0
713 | Security Staff | 987506 | 987506 | 156291 | 156291 | 18 | 18 | 2 | 2
73 | Regulatory Costs | 126476 | 126476 | 28010 | 28010 | 2 | 2 | 0 | 0
75 | Capital Plant Expenditures | 6346552 | 1993252 | 613862 | 333726 | 118 | 37 | 11 | 6
751 | Annualized RPV Replacements | 207929 | 53662 | 33883 | 8744 | 3 | 0 | 0 | 0
752 | Annualized Core Barrel Replacements | 1786828 | 461145 | 260135 | 67135 | 33 | 8 | 4 | 1
753 | Annualized Moderator Replacements | 154157 | 27240 | 24624 | 4351 | 2 | 0 | 0 | 0
754 | Annualized Reflector Replacements | 2098 | 370 | 416 | 73 | 0 | 0 | 0 | 0
755 | Annualized Reactivity Control Replacements | 1460240 | 235322 | 147752 | 23615 | 27 | 4 | 2 | 0
759 | Annualized Misc. Replacements | 2735297 | 1215510 | 542429 | 326412 | 50 | 22 | 10 | 6
78 | Annualized Decommissioning Cost | 70848 | 39571 | 8713 | 5409 | 1 | 0 | 0 | 0
80 | Annualized Fuel Cost | 1009924 | 1009924 | 188715 | 188715 | 18 | 18 | 3 | 3
81 | Refueling Operations | 2173 | 2173 | 366 | 366 | 0 | 0 | 0 | 0
82 | Additional Nuclear Fuel | 948019 | 948019 | 188541 | 188541 | 17 | 17 | 3 | 3
83 | Spent Fuel Management | 59731 | 59731 | 9087 | 9087 | 1 | 1 | 0 | 0
OCC | Overnight Capital Cost | 164440520 | 90273905 | 20449044 | 12368346 | - | - | - | -
OCC per kW | Overnight Capital Cost per kW | 26522 | 14560 | 3298 | 1994 | - | - | - | -
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 159627228 | 85460614 | 20415464 | 12332283 | - | - | - | -
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 25746 | 13783 | 3292 | 1989 | - | - | - | -
TCI | Total Capital Investment | 167278737 | 91832018 | 20801991 | 12581821 | - | - | - | -
TCI per kW | Total Capital Investment per kW | 26980 | 14811 | 3355 | 2029 | - | - | - | -
AC | Annualized Cost | 8668687 | 4284109 | 671988 | 427196 | - | - | - | -
AC per MWh | Annualized Cost per MWh | 161 | 79 | 12 | 7 | - | - | - | -
LCOE | Levelized Cost Of Energy ($/MWh) | 383 | 201 | 38 | 23 | - | - | - | -
LCOH | Levelized Cost Of Heat ($/MWth) | 103 | 53 | 10 | 6 | - | - | - | -

## Parameters
Group | Parameter | Value | Units | Description | Source
--- SETTINGS ---
Settings | cross_sections_xml_location | /hpc-common/data/openmc/endfb-viii.0-hdf5/cross_sections.xml |  | File path to the OpenMC cross sections XML file on HPC | User Input
Settings | plotting | N |  | Whether to generate and save geometry plots (Y = yes, N = no) | User Input
Settings | simplified_chain_thermal_xml | /home/garcsamu/OpenMC/TEMA/data/chain_casl_pwr.xml |  | File path to the simplified depletion chain XML file for thermal reactors | User Input
--- MATERIALS ---
Materials | Axial Reflector | Graphite |  | Axial reflector material type — may differ from radial reflector | User Input
Materials | Common Temperature | 600 | K | Uniform operating temperature applied to all materials in isothermal simulations | User Input
Materials | Control Drum Absorber | B4C_enriched |  | Neutron absorber material in the control drums (e.g. B4C_enriched, B4C_natural) | User Input
Materials | Control Drum Reflector | Graphite |  | Reflector material in the control drums (e.g. Graphite) | User Input
Materials | Coolant | NaK |  | Primary coolant material type (e.g. NaK, Helium) | User Input
Materials | Enrichment | 0.1975 | fraction | Uranium-235 enrichment fraction (0 to 1) | User Input
Materials | Fuel | UZrH_alloy |  | Primary fuel material type (e.g. TRIGA_fuel, UO2, UN, UC, homog_TRISO) | User Input
Materials | HX Material | SS316 |  | Heat exchanger structural material (e.g. SS316) | User Input
Materials | H_Zr_ratio | 1.6 | atomic ratio | Ratio of hydrogen atoms to zirconium atoms in TRIGA fuel (ZrH hydride) | User Input
Materials | Moderator | ZrH |  | Neutron moderator material type (e.g. ZrH, Graphite, monolith_graphite) | User Input
Materials | Radial Reflector | Graphite |  | Radial reflector material type (e.g. Graphite, BeO) | User Input
Materials | TRISO Fueled | No |  | Whether the reactor uses TRISO fuel particles (Yes or No) | User Input
Materials | U_met_wo | 0.3 | weight fraction | Weight fraction of uranium metal in TRIGA fuel (remainder is ZrH matrix) | User Input
Materials | er_wo | 0 | weight fraction | Weight fraction of erbium burnable poison in TRIGA fuel (0 means no erbium) | User Input
Materials | reactor type | LTMR |  | Reactor type identifier: LTMR (liquid metal thermal), GCMR (gas-cooled), or HPMR (heat pipe) | User Input
--- GEOMETRY ---
Geometry | Active Height | 78.4 | cm | Axial height of the active fuel region | User Input
Geometry | Assembly FTF | 65.8006 | cm | Assembly flat-to-flat distance (distance between opposite parallel faces of the hexagonal assembly). | Calculated
Geometry | Axial Reflector Thickness | 14 | cm | Thickness of each axial neutron reflector (top and bottom) | User Input
Geometry | Core Radius | 46.9003 | cm | Total core radius including the radial reflector | Calculated
Geometry | Fuel Pin Count | 300 |  | Total number of fuel pins (or fuel elements) in the entire core | Calculated
Geometry | Fuel Pin Materials | ['Zr', None, 'UZrH_alloy', None, 'SS304'] |  | Ordered list of materials for each fuel pin region from innermost to outermost | User Input
Geometry | Fuel Pin Radii | [0.28575, 0.3175, 1.5113, 1.5367, 1.5875] | cm | Ordered list of radii defining fuel pin region boundaries from innermost to outermost | User Input
Geometry | Lattice Apothem | 32.9003 | cm | Distance from the hex lattice center to the midpoint of a flat face of the outermost pin lattice. | Calculated
Geometry | Lattice Radius | 32.9003 | cm | Legacy LTMR name for the hex lattice apothem: distance from the hex lattice center to the midpoint of a flat face. | Calculated
Geometry | Moderator Pin Count | 97 |  | Total number of moderator pins in the entire core | Calculated
Geometry | Moderator Pin Inner Radius | 1.5367 | cm | Inner radius of the moderator pin cladding | User Input
Geometry | Moderator Pin Materials | ['ZrH', 'SS304'] |  | Ordered list of materials for each moderator pin region from innermost to outermost | User Input
Geometry | Moderator Pin Radii | [1.5367, 1.5875] | cm | Ordered list of radii defining moderator pin region boundaries | User Input
Geometry | Number of Rings per Assembly | 12 |  | Number of pin rings along the side of the hexagonal assembly (LTMR/HPMR) | User Input
Geometry | Pin Gap Distance | 0.1 | cm | Gap distance between adjacent pins (center-to-center minus two outer radii) | User Input
Geometry | Radial Reflector Thickness | 14 | cm | Thickness of the radial neutron reflector surrounding the active core | User Input
--- CONTROL DRUMS ---
Control Drums | All Drums Area | 3326.2272 | cm² | Total cross-sectional area of all control drums | Calculated
Control Drums | All Drums Volume | 353910.57 | cm³ | Total volume of all control drums combined | Calculated
Control Drums | Control Drum Absorber Mass | 59.929 | kg | Total mass of absorber material in all control drums | Calculated
Control Drums | Control Drum Reflector Mass | 528.2068 | kg | Total mass of reflector material in all control drums | Calculated
Control Drums | Control Drums Mass | 588.1357 | kg | Total combined mass of all control drums (absorber + reflector) | Calculated
Control Drums | Drum Absorber Arc Degrees | 120 | degrees | Angular span of the absorber arc on each control drum | User Input
Control Drums | Drum Absorber Thickness | 1 | cm | Thickness of the absorber arc section within each control drum | User Input
Control Drums | Drum Count | 12 |  | Total number of control drums in the core | Calculated
Control Drums | Drum Height | 106.4 | cm | Height of the control drums (typically active height + 2x axial reflector thickness) | User Input
Control Drums | Drum Radius | 9.3931 | cm | Outer radius of each control drum. If not specified, it is automatically set to the largest allowable value that avoids drum overlap. | User Input
Control Drums | Number of Drums | 12 |  | Number of control drums in the core (e.g. 6, 12) | User Input
--- CORE DESIGN ---
Core Design | Axial Reflector Mass | 154.7923 | kg | Total mass of both axial reflectors (top and bottom combined) | Calculated
Core Design | Moderator Mass | 315.9395 | kg | Total mass of the neutron moderator material in the core | Calculated
Core Design | Radial Reflector Mass | -28.1758 | kg | Total mass of the radial neutron reflector | Calculated
--- OVERALL SYSTEM ---
Overall System | Burnup Steps | [0.1, 120.0, 140.0] | MWd/kg | Cumulative burnup values at each depletion time step | User Input
Overall System | Heat Flux | 0.85251 | MW/m² | Calculated average fuel surface heat flux at full power | Calculated
Overall System | Heat Flux Criteria | 0.9 | MW/m² | Maximum allowable fuel surface heat flux (design constraint) | User Input
Overall System | Power MWe | 6.2 | MWe | Reactor net electric power output (thermal power × thermal efficiency) | Calculated
Overall System | Power MWt | 20 | MWt | Reactor thermal power output | User Input
Overall System | Thermal Efficiency | 0.31 | fraction | Net thermal-to-electric conversion efficiency of the power conversion system | User Input
--- OPENMC SETTINGS ---
OpenMC Settings | Cold Shutdown Temperature | 300 | K | Temperature used for the shutdown-state (ARI) keff calculation during shutdown margin evaluation. | User Input
OpenMC Settings | Isothermal Temperature Coefficients | FALSE |  | Whether isothermal temperature reactivity coefficients were calculated | User Input
OpenMC Settings | Shutdown Margin Calc | FALSE |  | Whether shutdown margin is calculated. When True, the shutdown-state keff is evaluated with the absorber facing the core (ARI) at Cold Shutdown Temperature, and shutdown margin metrics are reported from ((1 - k_s) / k_s). | User Input
--- PHYSICS RESULTS ---
Physics Results | BOL Axial Non-Leakage Probability | 0.98866 | fraction | Beginning-of-life axial non-leakage probability from the 2D-to-3D buckling correction model. | Calculated
Physics Results | BOL Total Non-Leakage Probability | 0.95681 | fraction | Beginning-of-life total non-leakage probability from the axial-plus-radial buckling model. Returns NaN when Core Radius is not available. | Calculated
Physics Results | Depletion Time Steps | [0.0, 1.7274, 2072.8854, 2418.3662] | days | Calculated cumulative depletion times corresponding to the reported keff values and used as the x-axis in keff_comparison_vs_Time.png. | Calculated
Physics Results | Estimated Axial Leakage (%) | 1.134 | % | Estimated beginning-of-life axial neutron leakage percentage from the axial buckling correction model, computed as 100 × (1 - axial non-leakage probability). | Calculated
Physics Results | Estimated Total Leakage (%) | 4.3193 | % | Estimated beginning-of-life total neutron leakage percentage from the axial-plus-radial buckling model, computed as 100 × (1 - total non-leakage probability). Returns NaN when Core Radius is not available. | Calculated
Physics Results | Fuel Lifetime | 2360 | days | Estimated fuel cycle length — time for the 3D-corrected keff to fall to 1.0 | Calculated
Physics Results | Fuel Tail Waste Mass | 14299.9048 | kg | Mass of depleted uranium tails produced during the enrichment process | Calculated
Physics Results | Mass U235 | 67539.1073 | g | Initial mass of U-235 in the fresh fuel load | Calculated
Physics Results | Mass U238 | 277941.7848 | g | Initial mass of U-238 in the fresh fuel load | Calculated
Physics Results | Max Peaking Factor | 2.0473 | unitless | Maximum pin peaking factor across all depletion steps — the most limiting value over the fuel lifetime | Calculated
Physics Results | Max Peaking Factors per Step | [2.0269356637715483, 1.8838520581014018, 1.9740790899825835, 2.0473079645543466] | unitless | List of the maximum pin peaking factor at each depletion step, in step order | Calculated
Physics Results | Maximum Shutdown Margin 2D | N/A | pcm | Maximum shutdown margin from the 2D simulation, computed as max((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Maximum Shutdown Margin 3D (2D corrected) | N/A | pcm | Maximum shutdown margin corrected from 2D to 3D using axial neutron leakage correction, computed as max((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state corrected keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Most Limiting Shutdown Margin 2D | N/A | pcm | Most limiting shutdown margin from the 2D simulation, computed as min((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) | N/A | pcm | Most limiting shutdown margin corrected from 2D to 3D using axial neutron leakage correction, computed as min((1 - k_s) / k_s) over depletion steps, where k_s is the shutdown-state corrected keff with the absorber facing the core (ARI) at Cold Shutdown Temperature. | Calculated
Physics Results | Natural Uranium Mass | 14645.3856 | kg | Mass of natural uranium feed required to produce the enriched fuel | Calculated
Physics Results | Region ID with Max Peaking Factor | 165 | unitless | Region ID with the highest peaking factor across all depletion steps; for LTMR this is typically a pin/distribcell ID, while for GCMR it is a mesh-region index | Calculated
Physics Results | SWU | 14197.4432 | kg-SWU | Separative work units required to produce the enriched fuel | Calculated
Physics Results | Step with Max Peaking Factor | 4 | unitless | Depletion step number at which the maximum peaking factor occurs | Calculated
Physics Results | Temp Coeff 2D | N/A | pcm/K | Most limiting (least negative) isothermal temperature coefficient from the 2D simulation. Negative values indicate self-stabilizing behavior. Note: 2D simulation overestimates keff — use 3D corrected value for safety conclusions. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) | N/A | pcm/K | Most limiting (least negative) isothermal temperature coefficient corrected from 2D to 3D using axial neutron leakage correction. Negative values confirm self-stabilizing behavior. Use this value for safety analysis. | Calculated
Physics Results | Uranium Mass | 345.4809 | kg | Total initial uranium mass in the fresh fuel load (U-235 + U-238) | Calculated
Physics Results | keff 2D | [1.3870076026633278, 1.36004091729738, 1.0765817853025663, 0.9993686214130774] |  | keff at each burnup step for the operating configuration (ARO) from the 2D OpenMC simulation, evaluated at Common Temperature. | Calculated
Physics Results | keff 3D (2D corrected) | [1.3712794643599007, 1.3445279982439595, 1.0633864872943293, 0.9869859621443854] |  | keff at each burnup step for the operating configuration (ARO), corrected from 2D to 3D using axial leakage correction and evaluated at Common Temperature. | Calculated
--- PRIMARY LOOP & BALANCE OF PLANT ---
Primary Loop & Balance of Plant | BoP Count | 2 |  | Number of Balance of Plant (power conversion) systems | User Input
Primary Loop & Balance of Plant | BoP Power kWe | 3100 | kWe | Electric power handled by each BoP system | Calculated
Primary Loop & Balance of Plant | BoP per loop load fraction | 0.5 | fraction | Fraction of total electric load handled by each BoP system | User Input
Primary Loop & Balance of Plant | Coolant Mass Flow Rate | 226.2955 | kg/s | Total primary coolant mass flow rate | Calculated
Primary Loop & Balance of Plant | Primary HX Mass | 5208.2253 | kg | Calculated mass of the primary heat exchanger | Calculated
Primary Loop & Balance of Plant | Primary Loop Inlet Temperature | 703.15 | K | Primary coolant temperature at the core inlet | User Input
Primary Loop & Balance of Plant | Primary Loop Mass Flow Rate | 226.2955 | kg/s | Coolant mass flow rate per primary loop | Calculated
Primary Loop & Balance of Plant | Primary Loop Outlet Temperature | 793.15 | K | Primary coolant temperature at the core outlet | User Input
Primary Loop & Balance of Plant | Primary Pump | Yes |  | Whether a primary coolant pump is present (Yes or No) | User Input
Primary Loop & Balance of Plant | Primary Pump Mechanical Power | 94.2898 | kW | Mechanical power required to drive the primary coolant pump | Calculated
Primary Loop & Balance of Plant | Pump Isentropic Efficiency | 0.8 | fraction | Isentropic efficiency of the primary coolant pump | User Input
Primary Loop & Balance of Plant | Secondary HX Mass | 0 | kg | Mass of the secondary heat exchanger (0 if none) | User Input
Primary Loop & Balance of Plant | Secondary Loop Inlet Temperature | 668.15 | K | Secondary loop coolant temperature at the heat exchanger inlet | User Input
Primary Loop & Balance of Plant | Secondary Loop Outlet Temperature | 768.15 | K | Secondary loop coolant temperature at the heat exchanger outlet | User Input
Primary Loop & Balance of Plant | Secondary Pump | No |  | Whether a secondary coolant pump is present (Yes or No) | User Input
--- SHIELDING ---
Shielding | In Vessel Shield Inner Radius | 46.9003 | cm | Inner radius of the in-vessel radiation shield (equal to core radius) | User Input
Shielding | In Vessel Shield Mass | 1701.2498 | kg | Total mass of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Material | B4C_natural |  | Material of the in-vessel radiation shield | User Input
Shielding | In Vessel Shield Outer Radius | 57.0603 | cm | Outer radius of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Thickness | 10.16 | cm | Thickness of the in-vessel radiation shield (0 if none) | User Input
Shielding | Out Of Vessel Shield Effective Density Factor | 0.5 | fraction | Effective density factor for the out-of-vessel shield — accounts for partial fill (e.g. 0.5 = 50% fill) | User Input
Shielding | Out Of Vessel Shield Mass | 3257.546 | kg | Total mass of the out-of-vessel radiation shield | Calculated
Shielding | Out Of Vessel Shield Material | WEP |  | Material of the out-of-vessel radiation shield | User Input
Shielding | Out Of Vessel Shield Thickness | 39.37 | cm | Thickness of the out-of-vessel radiation shield | User Input
Shielding | Outer Shield Outer Radius | 113.9303 | cm | Outer radius of the out-of-vessel shield (outermost boundary of the shielded assembly) | Calculated
--- VESSELS ---
Vessels | Cooling Vessel Mass | 447.9755 | kg | Total mass of the cooling vessel | Calculated
Vessels | Cooling Vessel Material | stainless_steel |  | Structural material of the cooling vessel | User Input
Vessels | Cooling Vessel Radius | 69.0603 | cm | Outer radius of the cooling vessel | Calculated
Vessels | Cooling Vessel Thickness | 0.5 | cm | Wall thickness of the cooling vessel | User Input
Vessels | Gap Between Cooling Vessel And Intake Vessel | 5 | cm | Radial gap between the cooling vessel and intake vessel | User Input
Vessels | Gap Between Guard Vessel And Cooling Vessel | 5 | cm | Radial gap between the guard vessel and cooling vessel | User Input
Vessels | Gap Between Vessel And Guard Vessel | 5 | cm | Radial gap between the reactor vessel and guard vessel | User Input
Vessels | Guard Vessel Mass | 816.0567 | kg | Total mass of the guard vessel | Calculated
Vessels | Guard Vessel Material | stainless_steel |  | Structural material of the guard vessel | User Input
Vessels | Guard Vessel Radius | 64.0603 | cm | Outer radius of the guard vessel | Calculated
Vessels | Guard Vessel Thickness | 1 | cm | Wall thickness of the guard vessel (0 if none) | User Input
Vessels | Intake Vessel Mass | 490.0778 | kg | Total mass of the intake vessel | Calculated
Vessels | Intake Vessel Material | stainless_steel |  | Structural material of the intake vessel | User Input
Vessels | Intake Vessel Radius | 74.0603 | cm | Outer radius of the intake vessel | Calculated
Vessels | Intake Vessel Thickness | 0.5 | cm | Wall thickness of the intake vessel | User Input
Vessels | Total Vessels Mass | 3179.8932 | kg | Combined mass of all vessel components (pressure vessel, guard, cooling, intake) | Calculated
Vessels | Vessel Bottom Depth | 32.129 | cm | Depth of the vessel bottom head (ellipsoidal) | User Input
Vessels | Vessel Height | 203.552 | cm | Total height of the reactor pressure vessel | Calculated
Vessels | Vessel Lower Plenum Height | 50 | cm | Height of the lower plenum region below the active core | User Input
Vessels | Vessel Mass | 1425.7832 | kg | Total mass of the reactor pressure vessel | Calculated
Vessels | Vessel Material | stainless_steel |  | Structural material of the reactor pressure vessel | User Input
Vessels | Vessel Radius | 57.0603 | cm | Inner radius of the reactor pressure vessel (or core barrel) | User Input
Vessels | Vessel Thickness | 2 | cm | Wall thickness of the reactor pressure vessel | User Input
Vessels | Vessel Upper Gas Gap | 0 | cm | Height of the upper gas gap above the upper plenum (0 if none) | User Input
Vessels | Vessel Upper Plenum Height | 47.152 | cm | Height of the upper plenum region above the active core | User Input
Vessels | Vessels Total Height | 254.181 | cm | Total height of the complete vessel assembly | Calculated
Vessels | Vessels Total Radius | 74.5603 | cm | Total outer radius of the complete vessel assembly | Calculated
--- OPERATION ---
Operation | A75: Core Barrel Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled core barrel replacements | User Input
Operation | A75: Drum Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled control drum replacements | User Input
Operation | A75: Reflector Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled reflector replacements | User Input
Operation | A75: Vessel Replacement Period (cycles) | 1 | cycles | Number of fuel cycles between scheduled reactor pressure vessel replacements | User Input
Operation | A78: CAPEX to Decommissioning Cost Ratio | 0.15 | fraction | Ratio of total decommissioning cost to total capital cost (typical range: 9%–15%) | User Input
Operation | Annual Electricity Production | 53694.48 | MWh/year | Total annual electricity production at the calculated capacity factor | Calculated
Operation | Capacity Factor | 0.98863 | fraction | Annual plant capacity factor — fraction of the year the plant operates at full power | Calculated
Operation | Emergency Shutdowns Per Year | 0.2 | events/year | Expected number of unplanned emergency shutdowns per year | User Input
Operation | Levelization Period | 60 | years | Plant lifetime used for LCOE levelization (economic analysis period) | User Input
Operation | Maintenance to Direct Cost Ratio | 0.03 | fraction | Ratio of annual non-replacement maintenance cost to total direct capital cost | User Input
Operation | Number of Operators | 2 |  | Number of operators assigned per shift | User Input
Operation | Onsite Coolant Inventory | 36660 | kg | Total mass of coolant stored on site (fresh + used tanks) | User Input
Operation | Operation Mode | Remotely Monitored |  | Reactor operation mode: Remotely Monitored or On-Site Staffed | User Input
Operation | Reactors Monitored Per Operator | 10 |  | Number of reactors that can be monitored by a single operator | User Input
Operation | Refueling Period | 7 | days | Duration of the scheduled refueling outage | User Input
Operation | Replacement Coolant Inventory | 0 | kg | Mass of coolant replaced per refueling cycle | User Input
Operation | Security Staff Per Shift | 1 |  | Number of security personnel required per shift | User Input
Operation | Startup Duration after Emergency Shutdown | 14 | days | Duration of the startup sequence following an emergency shutdown | User Input
Operation | Startup Duration after Refueling | 2 | days | Duration of the startup sequence following a refueling outage | User Input
--- ECONOMIC PARAMETERS ---
Economic Parameters | Annual Return | 0.0475 | fraction | Annual return rate assumed for the decommissioning reserve fund | User Input
Economic Parameters | Assumed Number Of Units For Onsite Learning | 200 |  | Number of units assumed for onsite learning (typically 2 × NOAK Unit Number) | Calculated
Economic Parameters | Construction Duration | 12 | months | Duration of plant construction used for financing cost calculation | User Input
Economic Parameters | Control Building Basement Volume | 5.9448 | m³ | Volume of concrete in the control building basement | User Input
Economic Parameters | Control Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the control building exterior walls | User Input
Economic Parameters | Control Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the control building slab roof | User Input
Economic Parameters | Debt To Equity Ratio | 1 | fraction | Ratio of debt financing to equity financing for the project | User Input
Economic Parameters | Discount Rate | 0.07 | fraction | Annual discount rate (WACC) used for LCOE levelization and cost annualization | User Input
Economic Parameters | Emergency Building Basement Volume | 0 | m³ | Volume of concrete in the emergency building basement (0 if none) | User Input
Economic Parameters | Emergency Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the emergency building exterior walls (0 if none) | User Input
Economic Parameters | Emergency Building Slab Roof Volume | 0 | m³ | Volume of concrete in the emergency building slab roof (0 if none) | User Input
Economic Parameters | Escalation Year | 2025 | year | Reference year to which all costs are escalated for consistent comparison | User Input
Economic Parameters | Excavation Volume | 412.605 | m³ | Volume of earth to be excavated for plant construction | User Input
Economic Parameters | FTEs Per Offsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per offsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per onsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator Per Year | 0.017222 | FTE/operator/year | Total FTE-years per operator per year including all activities | Calculated
Economic Parameters | FTEs Per Operator Per Year Per Refueling | 0.0058333 | FTE/operator/year | Fraction of an FTE spent per operator per year on refueling-related activities | User Input
Economic Parameters | FTEs Per Security Staff (24/7) | 5 | FTE/staff | Full-time equivalents needed per security staff position to maintain 24/7 coverage | User Input
Economic Parameters | Hours Per FTE | 1800 | hours/year | Annual working hours per full-time equivalent employee | User Input
Economic Parameters | Integrated Heat Exchanger Building Basement Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building basement (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building exterior walls (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Slab Roof Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building slab roof (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Superstructure Area | 0 | m² | Floor area of the integrated heat exchanger building superstructure (0 if none) | User Input
Economic Parameters | Interest Rate | 0.07 | fraction | Annual cost of debt used to calculate interest during construction (Account 62) | User Input
Economic Parameters | Land Area | 18 | acres | Total land area required for the plant site | User Input
Economic Parameters | Manipulator Building Basement Volume | 17.8374 | m³ | Volume of concrete in the manipulator building basement | User Input
Economic Parameters | Manipulator Building Exterior Walls Volume | 15.9195 | m³ | Volume of concrete in the manipulator building exterior walls | User Input
Economic Parameters | Manipulator Building Slab Roof Volume | 4.7566 | m³ | Volume of concrete in the manipulator building slab roof | User Input
Economic Parameters | NOAK Unit Number | 100 |  | Nth-of-a-kind unit number used to calculate the learning curve cost multiplier | User Input
Economic Parameters | Number of Samples | 1000 |  | Number of Monte Carlo samples used for cost uncertainty quantification | User Input
Economic Parameters | Radwaste Building Basement Volume | 0 | m³ | Volume of concrete in the radioactive waste building basement (0 if none) | User Input
Economic Parameters | Radwaste Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the radioactive waste building exterior walls (0 if none) | User Input
Economic Parameters | Radwaste Building Slab Roof Volume | 0 | m³ | Volume of concrete in the radioactive waste building slab roof (0 if none) | User Input
Economic Parameters | Reactor Building Basement Volume | 95.0976 | m³ | Volume of concrete in the reactor building basement | User Input
Economic Parameters | Reactor Building Exterior Walls Volume | 129.9564 | m³ | Volume of concrete in the reactor building exterior walls | User Input
Economic Parameters | Reactor Building Slab Roof Volume | 95.0976 | m³ | Volume of concrete in the reactor building slab roof | User Input
Economic Parameters | Reactor Building Superstructure Area | 77 | m² | Floor area of the reactor building superstructure | User Input
Economic Parameters | Refueling Building Basement Volume | 0 | m³ | Volume of concrete in the refueling building basement (0 if none) | User Input
Economic Parameters | Refueling Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the refueling building exterior walls (0 if none) | User Input
Economic Parameters | Refueling Building Slab Roof Volume | 0 | m³ | Volume of concrete in the refueling building slab roof (0 if none) | User Input
Economic Parameters | Spent Fuel Building Basement Volume | 0 | m³ | Volume of concrete in the spent fuel building basement (0 if none) | User Input
Economic Parameters | Spent Fuel Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the spent fuel building exterior walls (0 if none) | User Input
Economic Parameters | Spent Fuel Building Slab Roof Volume | 0 | m³ | Volume of concrete in the spent fuel building slab roof (0 if none) | User Input
Economic Parameters | Storage Building Basement Volume | 11.76 | m³ | Volume of concrete in the storage building basement | User Input
Economic Parameters | Storage Building Exterior Walls Volume | 15.768 | m³ | Volume of concrete in the storage building exterior walls | User Input
Economic Parameters | Storage Building Slab Roof Volume | 11.76 | m³ | Volume of concrete in the storage building slab roof (houses operational spares) | User Input
Economic Parameters | Turbine Building Basement Volume | 5.9448 | m³ | Volume of concrete in the turbine building basement | User Input
Economic Parameters | Turbine Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the turbine building exterior walls | User Input
Economic Parameters | Turbine Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the turbine building slab roof | User Input
Economic Parameters | Work Hours Per Shift | 10 | hours | Duration of each work shift | User Input
Economic Parameters | indirect to direct field-related cost | 0.06539 | fraction | Ratio of indirect field (site) costs to total direct field costs — covers site supervision, temporary facilities, and other indirect site activities | User Input
--- LEARNING RATES ---
Learning Rates | Factory Be | 0.41505 | fraction | Learning rate for factory-manufactured beryllium components | User Input
Learning Rates | Factory Be Cost Multiplier | 0.028363 | fraction | NOAK cost multiplier for beryllium components based on Wright's Law | Calculated
Learning Rates | Factory BeO | 0.39915 | fraction | Learning rate for factory-manufactured beryllium oxide components | User Input
Learning Rates | Factory BeO Cost Multiplier | 0.033897 | fraction | NOAK cost multiplier for beryllium oxide components based on Wright's Law | Calculated
Learning Rates | Factory Drums | 0.24138 | fraction | Learning rate for factory-manufactured control drum components | User Input
Learning Rates | Factory Drums Cost Multiplier | 0.15955 | fraction | NOAK cost multiplier for factory-built control drums based on Wright's Law | Calculated
Learning Rates | Factory Other | 0.22963 | fraction | Learning rate for other factory-manufactured components | User Input
Learning Rates | Factory Other Cost Multiplier | 0.17671 | fraction | NOAK cost multiplier for other factory-built components based on Wright's Law | Calculated
Learning Rates | Factory Primary Structure | 0.18443 | fraction | Learning rate for factory-manufactured primary structural components | User Input
Learning Rates | Factory Primary Structure Cost Multiplier | 0.25808 | fraction | NOAK cost multiplier for factory-built primary structure based on Wright's Law | Calculated
Learning Rates | Licensing Learning | 0 | fraction | Learning rate for licensing costs per doubling of cumulative units produced | User Input
Learning Rates | Licensing Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for licensing costs based on Wright's Law | Calculated
Learning Rates | No Learning | 0 | fraction | Learning rate for components with no learning benefit (fixed costs, rate = 0) | User Input
Learning Rates | No Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for components with no learning (always 1.0) | Calculated
Learning Rates | Non-nuclear off-the-shelf | 0.05 | fraction | Learning rate for non-nuclear commercial off-the-shelf components | User Input
Learning Rates | Non-nuclear off-the-shelf Cost Multiplier | 0.71121 | fraction | NOAK cost multiplier for non-nuclear commercial components based on Wright's Law | Calculated
Learning Rates | Onsite Learning | 0.08 | fraction | Learning rate for onsite construction and installation activities | User Input
Learning Rates | Onsite Learning Cost Multiplier | 0.57466 | fraction | NOAK cost multiplier for onsite construction activities based on Wright's Law | Calculated
--- DEBUG / INTERMEDIATE VALUES ---
Debug / Intermediate Values | keff 2D ARO (BOL) | 1.387 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — beginning of life | Calculated
Debug / Intermediate Values | keff 2D ARO (EOL) | 0.99937 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — end of life | Calculated
Debug / Intermediate Values | keff 2D ARO (min) | 0.99937 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 2D ARO (max) | 1.387 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO) from the 2D simulation, evaluated at Common Temperature. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (BOL) | 1.3713 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (EOL) | 0.98699 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (min) | 0.98699 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (max) | 1.3713 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — maximum value | Calculated
--- UNCATEGORIZED ---
Uncategorized | Outer Shield Inner Radius | 74.5603 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | PF Per Step | {1: Region_ID Peaking_Factor Step 0 0 0.531132 1 1 1 0.584608 1 2 2 0.662147 1 3 3 0.802190 1 4 4 0.628535 1 .. ... ... ... 295 295 0.895608 1 296 296 0.827607 1 297 297 0.703249 1 298 298 0.592311 1 299 299 0.618949 1 [300 rows x 3 columns], 2: Region_ID Peaking_Factor Step 0 0 0.453169 2 1 1 0.623180 2 2 2 0.621905 2 3 3 0.757473 2 4 4 0.700019 2 .. ... ... ... 295 295 0.878930 2 296 296 1.048822 2 297 297 0.695067 2 298 298 0.754415 2 299 299 0.741520 2 [300 rows x 3 columns], 3: Region_ID Peaking_Factor Step 0 0 0.587378 3 1 1 0.524199 3 2 2 0.558639 3 3 3 0.742589 3 4 4 0.627440 3 .. ... ... ... 295 295 0.800776 3 296 296 0.732409 3 297 297 0.718900 3 298 298 0.585186 3 299 299 0.601914 3 [300 rows x 3 columns], 4: Region_ID Peaking_Factor Step 0 0 0.498079 4 1 1 0.529911 4 2 2 0.669734 4 3 3 0.778592 4 4 4 0.709052 4 .. ... ... ... 295 295 0.811914 4 296 296 0.617779 4 297 297 0.812670 4 298 298 0.694217 4 299 299 0.570853 4 [300 rows x 3 columns]} |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | XS_type | endf8.0 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown